## 线管桥架计算
常用线缆穿管、桥架计算
《民用建筑电气设计标准》GB 51348-2019 | 弱电线管 | 26.5.7 1 单根25对及以上的大对数对绞电缆、12芯及以上光缆或单根其他弱电主干线缆，当在1根直线导管内敷设时，其管径利用率不宜大于50%；当在1根弯曲段导管内敷设时，其管径利用率不宜大于40%。 | [9 empty] | 40% |  |  | 选择管材类型 | 套接紧定式钢管（JDG）
|  | 26.5.7 2 同一根导管内敷设多根4对对绞电缆或多根4芯及以下配线光缆或多根其他弱电线缆时，其管径截面积利用率不应大于30%。 | [9 empty] | 30% |  |  | 弱电线缆
| 弱电桥架 | 26.5.7 3 同一根槽盒内可同时敷设多根电缆或光缆，其电缆槽盒截面积利用率不应大于50%。 | [9 empty] | 50% |  |  | 线缆总根数 | 1 |  |  |  | 线缆总截面积 | 18.0956
[15 empty] | 建议管径 | Φ16 |  |  |  | 线管截面积 | 132
[15 empty] | 建议桥架规格 | 50*50 |  |  |  | 桥架截面积 | 2500
光缆 | 外径 | 截面积 | 根数 | 建议管径 | 铜缆 | 外径 | 截面积 | 根数 | 建议管径 | 信号线 | 外径 | 截面积 | 根数 | 建议管径 | 信号线 | 外径 | 截面积 | 根数 | 建议管径 | 话筒线 | 外径 | 截面积 | 根数 | 建议管径
2芯皮线光缆 | 3 | 6 |  | - | UTP-CAT.5E | 5.3 | 22.0618 |  | - | RVV-2*0.5 | 5.9 | 27.3397 |  | - | RVVP-2*0.5 | 6.8 | 36.3168 |  | - | HTP-2*20/0.10 | 6 | 28.2743 |  | -
2芯室内光缆 | 4 | 12.5664 |  | - | FTP-CAT.5E | 6.5 | 33.1831 |  | - | RVV-2*0.75 | 6.3 | 31.1725 |  | - | RVVP-2*0.75 | 7.4 | 43.0084 |  | - | HTP-2*27/0.10 | 6 | 28.2743 |  | -
4芯室内光缆 | 4.8 | 18.0956 | 1 | #NAME? | SFTP-CAT.5E | 7 | 38.4845 |  | - | RVV-2*1.0 | 7.5 | 44.1786 |  | - | RVVP-2*1.0 | 8.2 | 52.8102 |  | - | HTP-2*37/0.10 | 6 | 28.2743 |  | -
6芯室内光缆 | 5.1 | 20.4282 |  | - | UTP-CAT.6 | 6 | 28.2743 |  | - | RVV-2*1.5 | 8.6 | 58.088 |  | - | RVVP-2*1.5 | 9.2 | 66.4761 |  | - | HTP-2*48/0.10 | 6 | 28.2743 |  | -
8芯室内光缆 | 5.6 | 24.6301 |  | - | FTP-CAT.6 | 7.6 | 45.3646 |  | - | RVV-2*2.5 | 10.6 | 88.2473 |  | - | RVVP-2*2.5 | 11.7 | 107.5132 |  | - | HTP-3*20/0.10 | 6.15 | 29.7057 |  | -
12芯室内光缆 | 6.2 | 30.1907 |  | - | U/FTP-CAT.6 | 8 | 50.2655 |  | - |  |  | 0 |  | - | RVVP-4*0.5 | 8.9 | 62.2114 |  | - | HTP-3*27/0.10 | 6.05 | 28.7475 |  | -
24芯室内光缆 | 8.1 | 51.53 |  | - | SFTP-CAT.6 | 8 | 50.2655 |  | - | RVV-4*0.75 | 8.3 | 54.1061 |  | - | RVVP-4*0.75 | 9.3 | 67.9291 |  | - |  |  | 0 |  | -
36芯室内光缆 | 14.5 | 165.13 |  | - | UTP-CAT.6A | 8.4 | 55.4177 |  | - | RVV-4*1.0 | 9 | 63.6173 |  | - | RVVP-4*1.0 | 10.5 | 86.5901 |  | - | 音响线 | 外径 | 截面积 | 根数 | 建议管径
48芯室内光缆 | 14.8 | 172.0336 |  | - | FTP-CAT.6A | 7.3 | 41.8539 |  | - | RVV-4*1.5 | 10.5 | 86.5901 |  | - | RVVP-4*1.5 | 11.5 | 103.8689 |  | - | GYX-2*1.0 | 8.4 | 55.4177 |  | -
72芯室内光缆 | 17.5 | 240.5282 |  | - | U/FTP-CAT.6A | 7.5 | 44.1786 |  | - | RVV-4*2.5 | 12.5 | 122.7185 |  | - | RVVP-4*2.5 | 13.6 | 145.2672 |  | - | GYX-2*1.5 | 8.72 | 59.7204 |  | -
96芯室内光缆 | 20.7 | 336.5353 |  | - | SFTP-CAT.6A | 8.2 | 52.8102 |  | - |  |  | 0 |  | - | RVVP-6*0.5 | 10.2 | 81.7128 |  | - | GYX-2*2.0 | 9.14 | 65.6118 |  | -
144芯室内光缆 | 24.8 | 483.0513 |  | - | S/FTP-CAT.7 | 7.5 | 44.1786 |  | - | RVV-6*0.75 | 9.6 | 72.3823 |  | - | RVVP-6*0.75 | 10.7 | 89.9202 |  | - | GYX-2*2.5 | 9.62 | 72.6842 |  | -
|  | 0 |  | - | S/FTP-CAT.7A | 7.8 | 47.7836 |  | - | RVV-6*1.0 | 11 | 95.0332 |  | - | RVVP-6*1.0 | 12.4 | 120.7628 |  | - | GYX-2*3.0 | 10.9 | 93.3132 |  | -
2~30芯室外光缆 | 7.8 | 47.7836 |  | - | S/FTP-CAT.8 | 8.2 | 52.8102 |  | - | RVV-6*1.5 | 13.3 | 138.9291 |  | - | RVVP-6*1.5 | 13.6 | 145.2672 |  | - | GYX-2*3.5 | 11.32 | 100.6428 |  | -
32~36芯室外光缆 | 8.1 | 51.53 |  | - |  |  | 0 |  | - | RVV-6*2.5 | 15.8 | 196.0668 |  | - | RVVP-6*2.5 | 16.1 | 203.5831 |  | - | GYX-2*4.0 | 12.08 | 114.6103 |  | -
38~60芯室外光缆 | 9.2 | 66.4761 |  | - | HBYV-1*2*0.4 | 2.55 | 4.4625 |  | - |  |  | 0 |  | - | RVVP-8*0.5 | 11.2 | 98.5203 |  | - |  |  | 0 |  | -
62~72芯室外光缆 | 9.6 | 72.3823 |  | - | HBYV-1*2*0.5 | 2.77 | 5.1799 |  | - | RVV-8*0.75 | 10.6 | 88.2473 |  | - | RVVP-8*0.75 | 11.8 | 109.3588 |  | - | 同轴线缆 | 外径 | 截面积 | 根数 | 建议管径
74~96芯室外光缆 | 11 | 95.0332 |  | - | HBYV-2*2*0.4 | 4.2 | 12.81 |  | - | RVV-8*1.0 | 13.2 | 136.8478 |  | - | RVVP-8*1.0 | 13.7 | 147.4114 |  | - | SYV-75-5 | 7.5 | 44.1786 |  | -
98~120芯室外光缆 | 12 | 113.0973 |  | - | HBYV-2*2*0.5 | 4.7 | 14.335 |  | - | RVV-8*1.5 | 14.2 | 158.3677 |  | - | RVVP-8*1.5 | 15 | 176.7146 |  | - | SYV-75-7 | 11.6 | 105.6832 |  | -
122~144芯室外光缆 | 13.2 | 136.8478 |  | - |  |  | 0 |  | - | RVV-8*2.5 | 17.7 | 246.0574 |  | - | RVVP-8*2.5 | 18 | 254.469 |  | - | SYV-75-9 | 12.6 | 124.6898 |  | -
146~216芯室外光缆 | 13.7 | 147.4114 |  | - | 3类25对大对数 | 11.6 | 105.6832 |  | - |  |  | 0 |  | - |  |  | 0 |  | - | SYV-75-12 | 15.4 | 186.265 |  | -
288芯室外光缆 | 15.5 | 188.6919 |  | - | 3类50对大对数 | 16.5 | 213.8246 |  | - | RVS-2*0.5 | 6 | 28.2743 |  | - | RVSP-2*0.5 | 6.9 | 37.3928 |  | - | SYWV-75-5 | 7.5 | 44.1786 |  | -
|  | 0 |  | - | 3类100对大对数 | 21.2 | 352.9894 |  | - | RVS-2*0.75 | 6.2 | 30.1907 |  | - | RVSP-2*0.75 | 7.4 | 43.0084 |  | - | SYWV-75-7 | 10.6 | 88.2473 |  | -
|  | 0 |  | - | 5类25对大对数 | 12.5 | 122.7185 |  | - | RVS-2*1.0 | 6.6 | 34.2119 |  | - | RVSP-2*1.0 | 8.2 | 52.8102 |  | - | SYWV-75-9 | 12.6 | 124.6898 |  | -
|  | 0 |  | - | 1/2"馈线 HCAAYZ 50-12射频同轴电缆 | 15.7 | 193.5928 |  | - | RVS-2*1.5 | 7.2 | 40.715 |  | - | RVSP-2*1.5 | 9.4 | 69.3978 |  | - |  |  | 0 |  | -
|  | 0 |  | - |  |  | 0 |  | - | RVS-2*2.5 | 8.2 | 52.8102 |  | - | RVSP-2*2.5 | 11.5 | 103.8689 |  | - | 电梯随行电缆 | 外径 | 截面积 | 根数 | 建议管径
|  | 0 |  | - |  |  | 0 |  | - |  |  | 0 |  | - |  |  | 0 |  | - | TUTP-G1 | 22 | 187 |  | -
|  | 0 |  | - |  |  | 0 |  | - |  |  | 0 |  | - |  |  | 0 |  | - | TGDFH2B6+2*1.0-G1 | 19.5 | 87.75 |  | -

## 基础数据
19DX101-1 表14.2 同轴电缆规格 |  |  | 19DX101-1 表6.55 0.45/0.75KV BV、BV-105、ZR-BV、NH-BV、WDZ-BYJ(F)、WDZN-BYJ(F)、WDZ-GYJS(F)、WDZN-GYJS(F)电线外径与截面积关系表 |  |  |  | 19DX101-1 表6.61 管材规格 | [9 empty] | 常用桥架规格
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2） | 线缆型号 0.45/0.75KV |  | 参考外径 （mm） | 电缆截面积 （mm2） | 管材种类 （标注代号） | 公称口径 （mm） | 外径 （mm） | 最小公称壁厚 （mm） | 内径 （mm） | 内孔截面积 （mm2） | 电线电缆可占用内孔截面积（mm2） |  |  |  | 桥架规格 | 宽 （mm） | 高 （mm） | 截面积（mm2）
SYV-75-5 | 7.5 | 44 | BV、BV-105、ZR-BV、NH-BV、WDZ-BYJ(F)、WDZN-BYJ(F)、WDZ-GYJS(F)、WDZN-GYJS(F) | 1 | 3.1 | 8 | [6 empty] | 40% | 33% | 27.5% | 22%
SYV-75-7 | 11.6 | 106 |  | 1.5 | 3.8 | 11 | 低压流体输送用焊接钢管 （SC） | DN15 | 21.3 | 2.2 | 16.9 | 224 | 89 | 73 | 61 | 49 | 50*50 | 50 | 50 | 2500
SYV-75-9 | 12.6 | 125 |  | 2.5 | 4.4 | 15 |  | DN20 | 26.9 | 2.2 | 22.5 | 397 | 158 | 131 | 109 | 87 | 100*50 | 100 | 50 | 5000
SYV-75-12 | 15.4 | 186 |  | 4 | 4.9 | 19 |  | DN25 | 33.7 | 2.5 | 28.7 | 646 | 258 | 213 | 177 | 142 | 100*100 | 100 | 100 | 10000
SYWV-75-5 | 7.5 | 44 |  | 6 | 5.4 | 23 |  | DN32 | 42.4 | 2.5 | 37.4 | 1098 | 439 | 362 | 301 | 241 | 150*100 | 150 | 100 | 15000
SYWV-75-7 | 10.6 | 88 |  | 10 | 7 | 38 |  | DN40 | 48.3 | 2.75 | 42.8 | 1437 | 574 | 474 | 395 | 316 | 200*100 | 200 | 100 | 20000
SYWV-75-9 | 12.6 | 125 |  | 16 | 8.1 | 52 |  | DN50 | 60.3 | 3 | 54.3 | 2314 | 925 | 763 | 636 | 509 | 300*100 | 300 | 100 | 30000
SYWLV-75-9 | 12.6 | 125 |  | 25 | 10.2 | 82 |  | DN65 | 76.1 | 3 | 70.1 | 3857 | 1542 | 1272 | 1060 | 848 | 400*100 | 400 | 100 | 40000
SYWLV-75-12 | 15.4 | 186 |  | 35 | 11.7 | 107 |  | DN80 | 88.9 | 3.25 | 82.4 | 5329 | 2131 | 1758 | 1465 | 1172 | 300*150 | 300 | 150 | 45000
SYDLY-75-9 | 11.9 | 111 |  | 50 | 13.9 | 152 |  | DN100 | 114.3 | 3.25 | 107.8 | 9122 | 3648 | 3010 | 2508 | 2006 | 500*100 | 500 | 100 | 50000
SYDLY-75-12 | 15 | 177 |  | 70 | 16 | 201 |  | DN125 | 139.7 | 3.5 | 132.7 | 13823 | 5529 | 4561 | 3801 | 3041 | 300*200 | 300 | 200 | 60000
SYDLY-75-14 | 16.7 | 219 |  | 95 | 18.2 | 260 |  | DN150 | 165.1 | 3.5 | 158.1 | 19621 | 7848 | 6474 | 5395 | 4316 | 400*150 | 400 | 150 | 60000
19DX101-1 表14.3 HYA型电话电缆规格 |  |  |  | 120 | 20.2 | 320 |  | DN200 | 219.1 | 4 | 211.1 | 34982 | 13992 | 11544 | 9620 | 7696 | 600*100 | 600 | 100 | 60000
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2） |  | 150 | 22.5 | 397 | 套接紧定式钢管 （JDG） CECS 120:2007 | Φ16 | 16 | 1.5 | 13 | 132 | 53 | 43 | 36 | 29 | 500*150 | 500 | 150 | 75000
HYA-5*2*0.5 | 11.5 | 104 |  | 185 | 24.9 | 487 |  | Φ20 | 20 | 1.6 | 16.8 | 222 | 88 | 73 | 61 | 49 | 400*200 | 400 | 200 | 80000
HYA-10*2*0.5 | 12.5 | 123 |  | 240 | 28.4 | 633 |  | Φ25 | 25 | 1.6 | 21.8 | 373 | 149 | 123 | 103 | 82 | 800*100 | 800 | 100 | 80000
HYA-15*2*0.5 | 14.5 | 165 | 19DX101-1 表6.56 电力电缆外径与截面积关系表 |  |  |  |  | Φ32 | 32 | 1.6 | 28.8 | 651 | 260 | 215 | 179 | 143 | 600*150 | 600 | 150 | 90000
HYA-20*2*0.5 | 15 | 177 | 线缆型号 0.6/1KV |  | 参考外径 （mm） | 电缆截面积 （mm2） |  | Φ40 | 40 | 1.6 | 36.8 | 1063 | 425 | 351 | 292 | 234 | 500*200 | 500 | 200 | 100000
HYA-25*2*0.5 | 16 | 201 | YJV、YJLV、ZR-YJV、WDZ-YJ(F)E | 5*2.5 | 13.5 | 143 |  | Φ50 | 50 | 1.6 | 46.8 | 1719 | 687 | 567 | 472 | 378 | 1000*100 | 1000 | 100 | 100000
HYA-30*2*0.5 | 17 | 227 |  | 5*4 | 14.8 | 172 | 聚氯乙烯硬质电线管 （PC） GA 305-2001 | Φ16 | 16 | 1.9 | 12.2 | 117 | 47 | 39 | 32 | 26 | 600*200 | 600 | 200 | 120000
HYA-50*2*0.5 | 20 | 314 |  | 5*6 | 16.1 | 204 |  | Φ20 | 20 | 2.1 | 15.8 | 196 | 78 | 65 | 54 | 43 | 800*150 | 800 | 150 | 120000
HYA-100*2*0.5 | 25.5 | 511 |  | 5*10 | 19.6 | 302 |  | Φ25 | 25 | 2.2 | 20.6 | 333 | 133 | 110 | 92 | 73 | 1000*150 | 1000 | 150 | 150000
HYA-200*2*0.5 | 32.5 | 830 |  | 5*18 | 22.4 | 394 |  | Φ32 | 32 | 2.7 | 26.6 | 556 | 222 | 183 | 153 | 122 | 800*200 | 800 | 200 | 160000
HYA-300*2*0.5 | 38 | 1134 |  | 4*25+1*16 | 26.2 | 539 |  | Φ40 | 40 | 2.8 | 34.4 | 929 | 371 | 307 | 255 | 204 | 1000*200 | 1000 | 200 | 200000
HYA-400*2*0.5 | 43.5 | 1486 |  | 4*35+1*16 | 28.8 | 651 |  | Φ50 | 50 | 3.4 | 43.2 | 1465 | 586 | 483 | 402 | 322
HYA-500*2*0.5 | 47.5 | 1772 |  | 4*50+1*25 | 33.4 | 876 | 聚氯乙烯半硬质电线管 （FPC） | Φ16 | 16 | 2 | 12 | 113 | 45 | 37 | 31 | 25 | GB 51348-2019 《民用建筑电气设计标准》26.5.7
19DX101-1 表14.4 HYAT型电话电缆规格 |  |  |  | 4*70+1*35 | 38.8 | 1182 |  | Φ20 | 20 | 2 | 16 | 201 | 80 | 66 | 55 | 44
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2） |  | 4*95+1*50 | 44.1 | 1527 |  | Φ25 | 25 | 2.5 | 20 | 314 | 125 | 104 | 86 | 69
HYAT-5*2*0.5 | 12.5 | 123 |  | 4*120+1*70 | 49.5 | 1924 |  | Φ32 | 32 | 3 | 26 | 531 | 212 | 175 | 146 | 117
HYAT-10*2*0.5 | 14 | 154 |  | 4*150+1*70 | 54.1 | 2298 |  | Φ40 | 40 | 3 | 34 | 907 | 363 | 299 | 250 | 200
HYAT-15*2*0.5 | 16 | 201 |  | 4*185+1*95 | 60.5 | 2873 |  | Φ50 | 50 | 3 | 44 | 1519 | 608 | 502 | 418 | 335
HYAT-20*2*0.5 | 17 | 227 |  | 4*240+1*120 | 68.2 | 3651 | 19DX101-1 表14.36 聚氯乙烯（PVC-U）实壁管管材规格
HYAT-25*2*0.5 | 18 | 254 | VV、VLV、NH-YJV、WDZN-YJ(F)E | 5*2.5 | 15.2 | 181 | 管材种类 （标注代号） | 公称口径 （mm） | 外径 （mm） | 壁厚 （mm） | 内径 （mm） | 内孔截面积 （mm2） | 内孔%时截面积（mm2）
HYAT-30*2*0.5 | 19.5 | 299 |  | 5*4 | 17.8 | 249 | [6 empty] | 40% | 33% | 27.5% | 22%
HYAT-50*2*0.5 | 23 | 415 |  | 5*6 | 19.2 | 289 | 聚氯乙烯（PVC-U） | Φ40 | 40 | 1.6 | 36.8 | 1064 | 425 | 351 | 292 | 234
HYAT-100*2*0.5 | 29 | 661 |  | 5*10 | 22.8 | 408 |  | Φ50 | 50 | 1.6 | 46.8 | 1720 | 688 | 568 | 473 | 378
HYAT-200*2*0.5 | 38.5 | 1164 |  | 5*18 | 25.8 | 523 |  | Φ63 | 63 | 1.8 | 59.4 | 2771 | 1108 | 914 | 762 | 610
HYAT-300*2*0.5 | 45.5 | 1626 |  | 4*25+1*16 | 30.1 | 711 |  | Φ75 | 75 | 2.8 | 69.4 | 3783 | 1513 | 1248 | 1040 | 832
HYAT-400*2*0.5 | 52 | 2124 |  | 4*35+1*16 | 32.7 | 839 |  | Φ90 | 90 | 2.2 | 85.6 | 5755 | 2302 | 1899 | 1583 | 1266
HYAT-500*2*0.5 | 56.5 | 2507 |  | 4*50+1*25 | 37.7 | 1116 |  | Φ100 | 100 | 2.6 | 94.8 | 7058 | 2823 | 2329 | 1941 | 1553 | GB 51348-2019 《民用建筑电气设计标准》8.3.3
19DX101-1 表14.5 光缆规格 |  |  |  | 4*70+1*35 | 41.9 | 1378 |  | Φ110 | 110 | 2.8 | 104.4 | 8560 | 3424 | 2825 | 2354 | 1883
规格 | 参考外径 （mm） | 电缆截面积 （mm2） |  | 4*95+1*50 | 47.6 | 1779 |  | Φ125 | 125 | 3.3 | 118.4 | 11010 | 4404 | 3633 | 3028 | 2422
2芯室内型 | 5.1 | 20 |  | 4*120+1*70 | 52 | 2123 |  | Φ140 | 140 | 3.5 | 133 | 13893 | 5557 | 4585 | 3821 | 3056
4芯室内型 | 5.6 | 25 |  | 4*150+1*70 | 56.8 | 2533 |  | Φ160 | 160 | 3.8 | 152.4 | 18241 | 7297 | 6020 | 5016 | 4013
6芯室内型 | 5.9 | 27 |  | 4*185+1*95 | 63 | 3116 | 注：表中的数据引自《地下通信管道用塑料管 第2部分：实壁管》YD/T 841.2-2016
8芯室内型 | 6.1 | 29 |  | 4*240+1*120 | 70.7 | 3924 | 19DX101-1 表14.37 聚乙烯（PE）实壁管管材规格
12芯室内型 | 7 | 38 | YJV22、YJLV22 | 5*2.5 | 17 | 227 | 管材种类 （标注代号） | 公称口径 （mm） | 外径 （mm） | 壁厚 （mm） | 内径 （mm） | 内孔截面积 （mm2） | 内孔%时截面积（mm2）
24芯室内型 | 14.8 | 172 |  | 5*4 | 18.3 | 263 | [6 empty] | 40% | 33% | 27.5% | 22%
48芯室内型 | 18.3 | 263 |  | 5*6 | 19.7 | 305 | 聚乙烯（PE） | Φ25 | 25 | 1.8 | 21.4 | 360 | 144 | 119 | 99 | 79
72/96芯室内型 | 22 | 380 |  | 5*10 | 23.2 | 423 |  | Φ32 | 32 | 1.8 | 28.4 | 633 | 253 | 209 | 174 | 139
144芯室内型 | 26.1 | 535 |  | 5*18 | 26 | 531 |  | Φ40 | 40 | 2 | 36 | 1018 | 407 | 336 | 280 | 224
2~24芯室外型 | 13.3 | 139 |  | 4*25+1*16 | 30.4 | 725 |  | Φ50 | 50 | 2.1 | 45.8 | 1647 | 659 | 544 | 453 | 362
48/72芯室外型 | 13.9 | 152 |  | 4*35+1*16 | 34.1 | 913 |  | Φ63 | 63 | 2.3 | 58.4 | 2679 | 1071 | 884 | 737 | 589
96芯室外型 | 15.8 | 196 |  | 4*50+1*25 | 38.7 | 1176 |  | Φ75 | 75 | 2.5 | 70 | 3848 | 1539 | 1270 | 1058 | 847
144芯室外型 | 20 | 314 |  | 4*70+1*35 | 44.2 | 1534 |  | Φ90 | 90 | 2.8 | 84.4 | 5595 | 2238 | 1846 | 1539 | 1231
19DX101-1 表14.6 4对对绞电缆规格 |  |  |  | 4*95+1*50 | 49.8 | 1947 |  | Φ100 | 100 | 3.8 | 92.4 | 6706 | 2682 | 2213 | 1844 | 1475
规格 | 参考外径 （mm） | 电缆截面积 （mm2） |  | 4*120+1*70 | 55.4 | 2409 |  | Φ110 | 110 | 4.2 | 101.6 | 8107 | 3243 | 2675 | 2230 | 1784
5类非屏蔽 | 12.5 | 123 |  | 4*150+1*70 | 60.1 | 2835 |  | Φ125 | 125 | 4.4 | 116.2 | 10605 | 4242 | 3500 | 2916 | 2333 | GB 51348-2019 《民用建筑电气设计标准》8.5.8
5类屏蔽 | 14 | 154 |  | 4*185+1*95 | 66.9 | 3513 |  | Φ140 | 140 | 4.6 | 130.8 | 13437 | 5375 | 4434 | 3695 | 2956
6类非屏蔽 | 16 | 201 |  | 4*240+1*120 | 74.8 | 4392 |  | Φ160 | 160 | 4.8 | 150.4 | 17766 | 7106 | 5863 | 4886 | 3908
6类屏蔽 | 17 | 227 | VV22、VLV22 | 5*2.5 | - | - | 注：表中的数据引自《地下通信管道用塑料管 第2部分：实壁管》YD/T 841.2-2016
6A类非屏蔽 | 18 | 254 |  | 5*4 | 21.1 | 349 | 19DX101-1 表14.38 双壁波纹管管材规格
6A类屏蔽 | 19.5 | 299 |  | 5*6 | 22.6 | 401 | 管材种类 （标注代号） | 公称口径 （mm） | 外径 （mm） | 壁厚 （mm） | 最小平均内径 （mm） | 内孔截面积 （mm2） | 内孔%时截面积（mm2）
7类屏蔽 | 23 | 415 |  | 5*10 | 26.2 | 539 | [6 empty] | 40% | 33% | 27.5% | 22%
7A类屏蔽 | 29 | 661 |  | 5*18 | 29.3 | 674 | 双壁波纹管 | Φ100 | 100 | - | 86 | 5809 | 2324 | 1917 | 1597 | 1278
8类屏蔽 | 38.5 | 1164 |  | 4*25+1*16 | 34.7 | 945 |  | Φ110 | 110 | - | 90 | 6362 | 2545 | 2099 | 1749 | 1400
19DX101-1 表14.7 大对数电缆（非屏蔽）规格 |  |  |  | 4*35+1*16 | 37.5 | 1104 |  | Φ125 | 125 | - | 105 | 8659 | 3464 | 2857 | 2381 | 1905
规格 | 参考外径 （mm） | 电缆截面积 （mm2） |  | 4*50+1*25 | 42.4 | 1411 |  | Φ140 | 140 | - | 118 | 10936 | 4374 | 3609 | 3007 | 2406
3类25对大对数 | 11.6 | 106 |  | 4*70+1*35 | 46.9 | 1727 |  | Φ160 | 160 | - | 134 | 14103 | 5641 | 4654 | 3878 | 3103
3类50对大对数 | 16.5 | 214 |  | 4*95+1*50 | 52.4 | 2155 |  | Φ200 | 200 | - | 167 | 21904 | 8762 | 7228 | 6024 | 4819
3类100对大对数 | 21.2 | 353 |  | 4*120+1*70 | 57.1 | 2559 | 注：表中的数据引自《地下通信管道用塑料管 第3部分：双壁波纹管》YD/T 841.3-2016
5类25对大对数 | 12.5 | 123 |  | 4*150+1*70 | 61.7 | 2988 | 19DX101-1 表14.39 塑料合金复合型管管材规格
19DX101-1 表14.8 RVVP、RVVPS型电线规格 |  |  |  | 4*185+1*95 | 67.9 | 3619 | 管材种类 （标注代号） | 公称口径 （mm） | 外径 （mm） | 壁厚 （mm） | 内径 （mm） | 内孔截面积 （mm2） | 内孔%时截面积（mm2）
线缆型号 | 参考外径 （mm） | 电缆截面积 （mm2） |  | 4*240+1*120 | 75.3 | 4451 | [6 empty] | 40% | 33% | 27.5% | 22%
RVVP-2*1.0 | 8.2 | 53 | 天正电气 电力电缆 |  |  |  | 塑料合金复合型管 | Φ62 | 62 | 2 | 58 | 2642 | 1057 | 872 | 727 | 581
RVVP-3*1.0 | 9.1 | 65 | 线缆型号 |  | 参考外径 （mm） | 电缆截面积 （mm2） |  | Φ92 | 92 | 3.2 | 85.6 | 5755 | 2302 | 1899 | 1583 | 1266
RVVP-5*1.0 | 11.3 | 100 | 3芯电力电缆 | 2.5 | 12.2 | 116.9 |  | Φ110 | 110 | 4 | 102 | 8171 | 3269 | 2697 | 2247 | 1798
RVVP-7*1.0 | 12.4 | 121 |  | 4 | 12.8 | 128.68 | 注：表中的数据引自《地下通信管道用塑料管 第8部分：塑料合金复合型管》YD/T 841.8-2014
RVVP-10*1.0 | 15.5 | 189 |  | 6 | 13.6 | 145.27 | 19DX101-1 表14.40 硅芯管管材规格
RVVP-12*1.0 | 16 | 201 |  | 10 | 16.2 | 206.12 | 管材种类 （标注代号） | 公称口径 （mm） | 外径 （mm） | 壁厚 （mm） | 内径 （mm） | 内孔截面积 （mm2） | 内孔%时截面积（mm2）
RVVP-2*1.5 | 9.2 | 66 |  | 16 | 18.6 | 271.72 | [6 empty] | 40% | 33% | 27.5% | 22%
RVVP-3*1.5 | 10 | 79 |  | 25 | 22.2 | 387.08 | 硅芯管 | 32/26 | 32 | 3 | 26 | 531 | 212 | 175 | 146 | 117
RVVP-5*1.5 | 12.6 | 125 |  | 35 | 24.1 | 456.17 |  | 34/28 | 34 | 3 | 28 | 616 | 246 | 203 | 169 | 135
RVVP-7*1.5 | 13.6 | 145 |  | 50 | 27.7 | 602.63 |  | 40/33 | 40 | 3.5 | 33 | 855 | 342 | 282 | 235 | 188
RVVP-10*1.5 | 16.9 | 224 |  | 70 | 32.1 | 809.28 |  | 46/38 | 46 | 4 | 38 | 1134 | 454 | 374 | 312 | 250
RVVP-12*1.5 | 17.7 | 246 |  | 95 | 36.4 | 1040.62 |  | 50/41 | 50 | 4.5 | 41 | 1320 | 528 | 436 | 363 | 290
RVVP-2*2.5 | 11.7 | 108 |  | 120 | 40.5 | 1288.25 |  | 63/54 | 63 | 4.5 | 54 | 2290 | 916 | 756 | 630 | 504
RVVP-3*2.5 | 12.6 | 125 |  | 150 | 44.6 | 1562.28 | 注：表中的数据引自《地下通信管道用塑料管 第4部分：硅芯管》YD/T 841.4-2016
RVVP-5*2.5 | 14.9 | 174 |  | 185 | 50 | 1963.5 | 19DX101-1 表14.41 梅花管管材规格
RVVP-7*2.5 | 16.1 | 204 |  | 240 | 56.1 | 2471.81 | 管材种类 （标注代号） | 型号 | 单孔内径 （mm） | 单孔截面积 （mm2） | 等效外径 （mm） | 等效截面积 （mm2） | 内孔%时截面积（mm2）
RVVP-10*2.5 | 20.2 | 320 |  | 300 | 60 | 2827.43 | [6 empty] | 40% | 33% | 27.5% | 22%
RVVP-12*2.5 | 21.3 | 356 | 3+1芯电力电缆 | 2.5 | 12.6 | 124.69 | 梅花管 | Φ25*5 | 25 | 491 | 76.1 | 2455 | 196 | 162 | 135 | 108
RVVP-2*4 | 13.9 | 152 |  | 4 | 13.4 | 141.03 |  | Φ26*5 | 26 | 531 | 78.8 | 2655 | 212 | 175 | 146 | 117
RVVP-3*4 | 14.9 | 174 |  | 6 | 14.6 | 167.42 |  | Φ28*4 | 28 | 616 | 76.2 | 2464 | 246 | 203 | 169 | 135
RVVPS-2*2*0.5 | 11.7 | 108 |  | 10 | 17.3 | 235.06 |  | Φ28*5 | 28 | 616 | 84.9 | 3080 | 246 | 203 | 169 | 135
RVVPS-2*2*0.75 | 12.8 | 129 |  | 16 | 20 | 314.16 |  | Φ32*4 | 32 | 804 | 86.5 | 3216 | 322 | 265 | 221 | 177
RVVPS-2*2*1.0 | 14.2 | 158 |  | 25 | 23.8 | 444.88 |  | Φ32*5 | 32 | 804 | 96.5 | 4020 | 322 | 265 | 221 | 177
RVVPS-2*2*1.5 | 15.4 | 186 |  | 35 | 25.8 | 522.79 |  | Φ32*7 | 32 | 804 | 117.3 | 5628 | 322 | 265 | 221 | 177
RVVPS-2*2*2.5 | 18.9 | 281 |  | 50 | 29.9 | 702.15 | 注：表中的数据引自《地下通信管道用塑料管 第5部分：梅花管》YD/T 841.5-2016
19DX101-1 表14.9 RVS、RV型电线规格 |  |  |  | 70 | 34.6 | 940.25
线缆型号 | 参考外径 （mm） | 电缆截面积 （mm2） |  | 95 | 39.3 | 1213.04 | CECS 100:1998 套接扣压式薄壁钢导管（KBG）
RVS-2*0.5 | 6 | 28 |  | 120 | 44.2 | 1534.39 | 管材种类 （标注代号） | 公称口径 （mm） | 外径 （mm） | 壁厚 （mm） | 内径 （mm） | 内孔截面积 （mm2） | 内孔%时截面积（mm2）
RVS-2*0.75 | 6.2 | 30 |  | 150 | 48 | 1809.56 | [6 empty] | 40% | 33% | 27.5% | 22%
RVS-2*1.0 | 6.6 | 34 |  | 185 | 53.8 | 2273.29 | 套接扣压式薄壁钢导管 （KBG） CECS 100:1998 | Φ16 | 16 | 1 | 14 | 153.938 | 61.5752 | 50.7996 | 42.333 | 33.8664
RVS-2*1.5 | 7.2 | 41 |  | 240 | 60.5 | 2874.75 |  | Φ20 | 20 | 1 | 18 | 254.469 | 101.7876 | 83.9748 | 69.979 | 55.9832
RVS-2*2.5 | 8.2 | 53 |  | 300 | 66.9 | 3515.14 |  | Φ25 | 25 | 1.2 | 22.6 | 401.15 | 160.46 | 132.3795 | 110.3162 | 88.253
RV-0.75 | 2.7 | 5.7 | 3+2芯电力电缆 | 2.5 | 13.2 | 136.85 |  | Φ32 | 32 | 1.2 | 29.6 | 688.1345 | 275.2538 | 227.0844 | 189.237 | 151.3896
RV-1.0 | 2.8 | 6.2 |  | 4 | 14.3 | 160.61 |  | Φ40 | 40 | 1.2 | 37.6 | 1110.3645 | 444.1458 | 366.4203 | 305.3502 | 244.2802
RV-1.5 | 3.4 | 9.1 |  | 6 | 15.6 | 191.13 | 注：KBG导管的壁厚不满足GB 50311-2016 《综合布线系统工程设计规范》7.5.8、GB 51348-2019 《民用建筑电气设计标准》26.5.4、26.5.5的要求，依据CECS 100:1998 《套接扣压式薄壁钢导管电线管路施工及验收规范》1.0.2 仅适用于1KV及以下无特殊规定的室内干燥场所。（个人理解：弱电智能化工程中仅适用于室内干燥场所墙面明敷）
RV-2.5 | 4.1 | 13.2 |  | 10 | 18.4 | 265.9
RV-4.0 | 4.8 | 18.1 |  | 16 | 21.4 | 359.68
19DX101-1 表14.10 RVV型电线规格 |  |  |  | 25 | 25.4 | 506.71 | GB 51348-2019 《民用建筑电气设计标准》26.5.4、26.5.5
线缆型号 | 参考外径 （mm） | 电缆截面积 （mm2） |  | 35 | 27.5 | 593.96
RVV-2*1.0 | 7.5 | 44 |  | 50 | 32.1 | 809.28
RVV-3*1.0 | 8 | 50 |  | 70 | 37.1 | 1081.03
RVV-5*1.0 | 9.8 | 75 |  | 95 | 42.2 | 1398.67
RVV-7*1.0 | 11 | 95 |  | 120 | 47.7 | 1787.01
RVV-10*1.0 | 14.5 | 165 |  | 150 | 51.4 | 2074.99
RVV-12*1.0 | 14.8 | 172 |  | 185 | 57.7 | 2614.82
RVV-2*1.5 | 8.6 | 58 |  | 240 | 64.9 | 3308.1
RVV-3*1.5 | 9.4 | 69 |  | 300 | 74 | 4300.84
RVV-5*1.5 | 11.6 | 106 | 4芯电力电缆 | 2.5 | 12.8 | 128.68
RVV-7*1.5 | 13.3 | 139 |  | 4 | 13.7 | 147.41
RVV-10*1.5 | 17.4 | 238 |  | 6 | 14.9 | 174.37
RVV-2*2.5 | 10.6 | 95 |  | 10 | 18 | 254.47
RVV-3*2.5 | 11.4 | 113 |  | 16 | 20.6 | 333.29
RVV-5*2.5 | 13.9 | 152 |  | 25 | 24.8 | 483.05
RVV-7*2.5 | 15.8 | 196 |  | 35 | 27.6 | 598.28
RVV-10*2.5 | 20.6 | 333 |  | 50 | 31.6 | 784.27
RVV-2*4 | 11.8 | 109 |  | 70 | 36.8 | 1063.62
RVV-3*4 | 12.4 | 121 |  | 95 | 41.8 | 1372.28
19DX101-1 表14.11 RVSVP型电线规格 |  |  |  | 120 | 46.5 | 1698.23
线缆型号 | 参考外径 （mm） | 电缆截面积 （mm2） |  | 150 | 51.6 | 2091.17
RVSVP-1*2*1.5 | 8.1 | 52 |  | 185 | 57.6 | 2605.76
RVSVP-1*2*2.5 | 9.9 | 77 |  | 240 | 64.9 | 3308.1
RVSVP-2*2*1.5 | 12.5 | 123 |  | 300 | 71.8 | 4048.92
RVSVP-2*2*2.5 | 15.5 | 189 | 4+1芯电力电缆 | 2.5 | 13.4 | 141.03
RVSVP-4*2*1.5 | 14.9 | 174 |  | 4 | 14.5 | 165.13
RVSVP-4*2*2.5 | 18.5 | 269 |  | 6 | 15.9 | 198.56
RVSVP-7*2*1.5 | 18.1 | 257 |  | 10 | 18.9 | 280.55
RVSVP-7*2*2.5 | 22.7 | 405 |  | 16 | 21.9 | 376.68
YD/T 1019-2013 四对对绞电缆 |  |  |  | 25 | 26.2 | 539.13
线缆型号 | 电缆最大外径 （mm） | 电缆截面积 （mm2） |  | 35 | 28.8 | 651.44 | GB 50311-2016 《综合布线系统工程设计规范》7.5.8
3类非屏蔽 | 6.3 | 31.17 |  | 50 | 33.4 | 876.16
3类屏蔽 | 7 | 38.48 |  | 70 | 38.8 | 1182.37
5类非屏蔽 | 6.3 | 31.17 |  | 95 | 44.1 | 1527.45
5类屏蔽 | 7 | 38.48 |  | 120 | 49.5 | 1924.42
5e类非屏蔽 | 6.3 | 31.17 |  | 150 | 54.1 | 2298.71
5e类屏蔽 | 7 | 38.48 |  | 185 | 60.5 | 2874.75
6类非屏蔽 | 6.3 | 31.17 |  | 240 | 68.2 | 3653.08
6类屏蔽 | 9 | 63.62 |  | 300 | 75.1 | 4429.65
6A类非屏蔽 | 9 | 63.62 | 5芯电力电缆 | 2.5 | 13.5 | 143.14
6A类屏蔽 | 9 | 63.62 |  | 4 | 14.8 | 172.03
7类屏蔽 | 9 | 63.62 |  | 6 | 16.1 | 203.58
7A类屏蔽 | 9 | 63.62 |  | 10 | 19.6 | 301.72
|  |  |  | 16 | 22.4 | 394.08
|  |  |  | 25 | 27.2 | 581.07
|  |  |  | 35 | 30.5 | 730.62
|  |  |  | 50 | 35 | 962.11
|  |  |  | 70 | 40.8 | 1307.41
|  |  |  | 95 | 46.4 | 1690.93
|  |  |  | 120 | 51.7 | 2099.28
|  |  |  | 150 | 57.4 | 2587.7
|  |  |  | 185 | 64.1 | 3227.05
|  |  |  | 240 | 72.3 | 4105.5
|  |  |  | 300 | 80 | 5026.55

## 飞鹤
RVS 300/300V 铜芯聚氯乙烯绝缘绞型连接用软电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
RVS-2*0.3 | 4.4 | 15.21
RVS-2*0.4 | 4.8 | 18.1
RVS-2*0.5 | 6 | 28.27
RVS-2*0.75 | 6.2 | 30.19
RVS-2*1.0 | 6.6 | 34.21
RVS-2*1.5 | 7.2 | 40.72
RVS-2*2.5 | 8.2 | 52.81
RVS-2*4 | 9.5 | 70.88
RVS-2*6 | 11.6 | 105.68
60227 IEC 52(RVV) 300/300V 轻型聚氯乙烯护套软线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
RVV-2*0.5 | 5.9 | 27.34
RVV-2*0.75 | 6.3 | 31.17
RVV-3*0.5 | 6.3 | 31.17
RVV-3*0.75 | 6.7 | 35.26
60227 IEC 53(RVV) 300/300V 轻型聚氯乙烯护套软线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
RVV-2*1.0 | 7.5 | 44.18
RVV-2*1.5 | 8.6 | 58.09
RVV-2*2.5 | 10.6 | 88.25
RVV-3*1.0 | 8 | 50.27
RVV-3*1.5 | 9.4 | 69.4
RVV-3*2.5 | 11.4 | 102.07
RVV-4*0.75 | 8.3 | 54.11
RVV-4*1.0 | 9 | 63.62
RVV-4*1.5 | 10.5 | 86.59
RVV-4*2.5 | 12.5 | 122.72
RVV-5*0.75 | 9.3 | 67.93
RVV-5*1.0 | 9.8 | 75.43
RVV-5*1.5 | 11.6 | 105.68
RVV-5*2.5 | 13.9 | 151.75
RVV 300/500V 铜芯聚氯乙烯绝缘聚乙烯护套软线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
RVV-2*4 | 12.4 | 120.76
RVV-2*6 | 13.9 | 151.75
RVV-2*10 | 17.2 | 232.35
RVV-3*4 | 13.5 | 143.14
RVV-3*6 | 15 | 176.71
RVV-3*10 | 18.8 | 277.59
RVV-4*4 | 14.6 | 167.42
RVV-4*6 | 16.4 | 211.24
RVV-4*10 | 20.5 | 330.06
RVV-5*4 | 16.5 | 213.82
RVV-5*6 | 18.4 | 265.9
RVV-5*10 | 22.9 | 411.87
RVV-6*0.75 | 9.6 | 72.38
RVV-6*1.0 | 11 | 95.03
RVV-6*1.5 | 13.3 | 138.93
RVV-6*2.5 | 15.8 | 196.07
RVV-7*0.75 | 9.6 | 72.38
RVV-7*1.0 | 11 | 95.03
RVV-7*1.5 | 13.3 | 138.93
RVV-7*2.5 | 15.8 | 196.07
RVV-8*0.75 | 10.6 | 88.25
RVV-8*1.0 | 13.2 | 136.85
RVV-8*1.5 | 14.2 | 158.37
RVV-8*2.5 | 17.7 | 246.06
RVV-10*0.5 | 12.1 | 114.99
RVV-10*0.75 | 13.2 | 136.85
RVV-10*1.0 | 14.5 | 165.13
RVV-10*1.5 | 17.4 | 237.79
RVV-10*2.5 | 20.6 | 333.29
RVV-12*0.5 | 11.2 | 98.52
RVV-12*0.75 | 13.2 | 136.85
RVV-12*1.0 | 14.8 | 172.03
RVV 300/500V 铜芯聚氯乙烯绝缘聚乙烯护套软线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
RVV-2*16 | 21 | 346.36
RVV-2*25 | 26.9 | 568.32
RVV-2*35 | 29.3 | 674.26
RVV-3*16 | 22.4 | 394.08
RVV-3*25 | 28.7 | 646.92
RVV-3*35 | 31.2 | 764.54
RVV-4*16 | 24.7 | 479.16
RVV-4*25 | 32.2 | 814.33
RVV-4*35 | 34.5 | 934.82
RVV-5*16 | 27.6 | 598.28
RVV-5*25 | 35.6 | 995.38
RVV-5*35 | 38.1 | 1140.09
RVVP 300/500V 铜芯聚氯乙烯绝缘编织屏蔽聚氯乙烯护套软线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
RVVP-2*0.3 | 6.2 | 30.19
RVVP-2*0.4 | 6.6 | 34.21
RVVP-2*0.5 | 6.8 | 36.32
RVVP-2*0.75 | 7.4 | 43.01
RVVP-2*1.0 | 8.2 | 52.81
RVVP-2*1.5 | 9.2 | 66.48
RVVP-2*2.5 | 11.7 | 107.51
RVVP-2*4 | 13.9 | 151.75
RVVP-3*0.3 | 6.5 | 33.18
RVVP-3*0.4 | 6.9 | 37.39
RVVP-3*0.5 | 7.1 | 39.59
RVVP-3*0.75 | 7.8 | 47.78
RVVP-3*1.0 | 9.1 | 65.04
RVVP-3*1.5 | 10 | 78.54
RVVP-3*2.5 | 12.6 | 124.69
RVVP-3*4 | 14.9 | 174.37
RVVP-4*0.3 | 7 | 38.48
RVVP-4*0.4 | 7.5 | 44.18
RVVP-4*0.5 | 8.9 | 62.21
RVVP-4*0.75 | 9.3 | 67.93
RVVP-4*1.0 | 10.5 | 86.59
RVVP-4*1.5 | 11.5 | 103.87
RVVP-4*2.5 | 13.6 | 145.27
RVVP-5*0.3 | 7.6 | 45.36
RVVP-5*0.4 | 8.1 | 51.53
RVVP-5*0.5 | 9.5 | 70.88
RVVP-5*0.75 | 10 | 78.54
RVVP-5*1.0 | 11.3 | 100.29
RVVP-5*1.5 | 12.6 | 124.69
RVVP-5*2.5 | 14.9 | 174.37
RVVP-6*0.3 | 8.2 | 52.81
RVVP-6*0.4 | 9.2 | 66.48
RVVP-6*0.5 | 10.2 | 81.71
RVVP-6*0.75 | 10.7 | 89.92
RVVP-6*1.0 | 12.4 | 120.76
RVVP-6*1.5 | 13.6 | 145.27
RVVP-6*2.5 | 16.1 | 203.58
RVVP-7*0.3 | 8.2 | 52.81
RVVP-7*0.4 | 9.2 | 66.48
RVVP-7*0.5 | 10.2 | 81.71
RVVP-7*0.75 | 10.7 | 89.92
RVVP-7*1.0 | 12.4 | 120.76
RVVP-7*1.5 | 13.6 | 145.27
RVVP-7*2.5 | 16.1 | 203.58
RVVP-8*0.3 | 9.1 | 65.04
RVVP-8*0.4 | 10.1 | 80.12
RVVP-8*0.5 | 11.2 | 98.52
RVVP-8*0.75 | 11.8 | 109.36
RVVP-8*1.0 | 13.7 | 147.41
RVVP-8*1.5 | 15 | 176.71
RVVP-8*2.5 | 18 | 254.47
RVVP-9*0.3 | 10.2 | 81.71
RVVP-9*0.4 | 10.9 | 93.31
RVVP-9*0.5 | 12 | 113.1
RVVP-9*0.75 | 12.7 | 126.68
RVVP-9*1.0 | 15 | 176.71
RVVP-9*1.5 | 16.1 | 203.58
RVVP-9*2.5 | 19.4 | 295.59
RVVP-10*0.3 | 10.9 | 93.31
RVVP-10*0.4 | 11.6 | 105.68
RVVP-10*0.5 | 13 | 132.73
RVVP-10*0.75 | 13.9 | 151.75
RVVP-10*1.0 | 15.5 | 188.69
RVVP-10*1.5 | 16.9 | 224.32
RVVP-10*2.5 | 20.2 | 320.47
RVVP-12*0.3 | 11.2 | 98.52
RVVP-12*0.4 | 11.9 | 111.22
RVVP-12*0.5 | 13.4 | 141.03
RVVP-12*0.75 | 14.3 | 160.61
RVVP-12*1.0 | 16 | 201.06
RVVP-12*1.5 | 17.7 | 246.06
RVVP-12*2.5 | 21.3 | 356.33
RVSP 300/300V 铜芯聚氯乙烯绝缘绞型连接用屏蔽软线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
RVSP-2*0.3 | 6.3 | 31.17
RVSP-2*0.4 | 6.7 | 35.26
RVSP-2*0.5 | 6.9 | 37.39
RVSP-2*0.75 | 7.4 | 43.01
RVSP-2*1.0 | 8.2 | 52.81
RVSP-2*1.5 | 9.4 | 69.4
RVSP-2*2.5 | 11.5 | 103.87
RVSP-2*4 | 13.9 | 151.75
RVSP-2*6 | 15.3 | 183.85
RVSP-3*0.3 | 6.6 | 34.21
RVSP-3*0.4 | 7.1 | 39.59
RVSP-3*0.5 | 7.2 | 40.72
RVSP-3*0.75 | 7.8 | 47.78
RVSP-3*1.0 | 9.1 | 65.04
RVSP-3*1.5 | 10.2 | 81.71
RVSP-3*2.5 | 12.4 | 120.76
RVSP-3*4 | 14.9 | 174.37
RVSP-3*6 | 16.2 | 206.12
JZ-BV-105型 450/750V 铜芯聚氯乙烯绝缘家装电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
BV-1.5 | 3.2 | 8.04
BV-2.5 | 3.9 | 11.95
BV-4 | 4.4 | 15.21
BV-6 | 5 | 19.63
JZ-BVR-105型 450/750V 铜芯聚氯乙烯绝缘家装电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
BVR-1.5 | 3.4 | 9.08
BVR-2.5 | 4.1 | 13.2
BVR-4 | 4.8 | 18.1
BVR-6 | 5.3 | 22.06
EC-BYJ(F)-125型 铜芯耐热125℃辐照交联聚烯烃绝缘电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
BYJ(F)-1.5 | 3.4 | 9.08
BYJ(F)-2.5 | 4.2 | 13.85
BYJ(F)-4 | 4.8 | 18.1
BYJ(F)-6 | 5.4 | 22.9
EC-BYJR(F)-125型 固定布线用铜芯耐热125℃辐照交联聚烯烃绝缘软电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
BYJR(F)-1.5 | 3.4 | 9.08
BYJR(F)-2.5 | 4.1 | 13.2
BYJR(F)-4 | 4.8 | 18.1
BYJR(F)-6 | 5.3 | 22.06
WDZB-BYJ 300/500V 铜芯交联聚烯烃绝缘无卤低烟阻燃B类电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB-BYJ-0.5 | 2.4 | 4.52
WDZB-BYJ-0.75 | 2.6 | 5.31
WDZB-BYJ-1.0 | 2.8 | 6.16
WDZB-BYJ 400/750V 铜芯交联聚烯烃绝缘无卤低烟阻燃B类电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB-BYJ-1.5 | 3.4 | 9.08
WDZB-BYJ-2.5 | 4.2 | 13.85
WDZB-BYJ-4 | 4.8 | 18.1
WDZB-BYJ-6 | 5.4 | 22.9
WDZB-BYJ-10 | 6.8 | 36.32
WDZB-BYJ-16 | 8 | 50.27
WDZB-BYJ-25 | 9.8 | 75.43
WDZB-BYJ-35 | 11 | 95.03
WDZB-BYJ-50 | 13 | 132.73
WDZB-BYJ-70 | 15 | 176.71
WDZB-BYJ-95 | 17 | 226.98
WDZB-BYJ-120 | 19 | 283.53
WDZB-BYJ-150 | 21 | 346.36
WDZB-BYJ-185 | 23.5 | 433.74
WDZB-BYJ-240 | 26.5 | 551.55
WDZB-BYJ-300 | 29.5 | 683.49
WDZB-BYJ-400 | 33.5 | 881.41
WDZB-BYJR 400/750V 铜芯交联聚烯烃绝缘无卤低烟阻燃B类软电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB-BYJR-2.5 | 4.1 | 13.2
WDZB-BYJR-4 | 4.8 | 18.1
WDZB-BYJR-6 | 5.3 | 22.06
WDZB-BYJR-10 | 7.3 | 41.85
WDZB-BYJR-16 | 8.6 | 58.09
WDZB-BYJR-25 | 10.2 | 81.71
WDZB-BYJR-35 | 11.7 | 107.51
WDZB-BYJR-50 | 13.9 | 151.75
WDZB-BYJR-70 | 16 | 201.06
WDZB-BYJR-95 | 18.2 | 260.16
WDZB-BYJR-120 | 20.2 | 320.47
WDZB-BYJR-150 | 22.5 | 397.61
WDZB-BYJR-185 | 24.9 | 486.95
WDZB-BYJR-240 | 28.4 | 633.47
WDZB-BYJR-300 | 31.2 | 764.54
WDZB-BYJR-400 | 35.5 | 989.8
WDZB-RYJ 300/500V 铜芯单芯软导体交联聚烯烃绝缘无卤低烟阻燃B类电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB-RYJ-0.5 | 2.5 | 4.91
WDZB-RYJ-0.75 | 2.7 | 5.73
WDZB-RYJ-1.0 | 2.8 | 6.16
WDZB-RYJ 450/750V 铜芯单芯软导体交联聚烯烃绝缘无卤低烟阻燃B类电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB-RYJ-1.5 | 3.4 | 9.08
WDZB-RYJ-2.5 | 4.1 | 13.2
WDZB-RYJ-4 | 4.8 | 18.1
WDZB-RYJ-6 | 5.3 | 22.06
WDZB-RYJ-10 | 6.8 | 36.32
WDZB-RYJ-16 | 8.1 | 51.53
WDZB-RYJ-25 | 10.2 | 81.71
WDZB-RYJ-35 | 11.7 | 107.51
WDZB-RYJ-50 | 13.9 | 151.75
WDZB-RYJ-70 | 16 | 201.06
WDZB-RYJ-95 | 18.2 | 260.16
WDZB-RYJ-120 | 20.2 | 320.47
WDZB-RYJ-150 | 22.5 | 397.61
WDZB-RYJ-185 | 24.9 | 486.95
WDZB-RYJ-240 | 28.4 | 633.47
WDZB-RYJS 300/300V 铜芯交联聚烯烃绝缘绞型连接用无卤低烟阻燃B类软电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB-RYJS-2*0.3 | 4.4 | 15.21
WDZB-RYJS-2*0.4 | 4.8 | 18.1
WDZB-RYJS-2*0.5 | 6 | 28.27
WDZB-RYJS-2*0.75 | 6.2 | 30.19
WDZB-RYJS-2*1.0 | 6.6 | 34.21
WDZB-RYJS-2*1.5 | 7.2 | 40.72
WDZB-RYJS-2*2.5 | 8.2 | 52.81
WDZB-RYJS-2*4 | 9.5 | 70.88
WDZB-RYJS-2*6 | 11.6 | 105.68
WDZB1-BYJ 300/500V 铜芯交联聚烯烃绝缘无卤低烟阻燃B1级电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB1-BYJ-0.5 | 2.4 | 4.52
WDZB1-BYJ-0.75 | 2.6 | 5.31
WDZB1-BYJ-1.0 | 2.8 | 6.16
WDZB1-BYJ 450/750V 铜芯交联聚烯烃绝缘无卤低烟阻燃B1级电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB1-BYJ-1.5 | 3.4 | 9.08
WDZB1-BYJ-2.5 | 4.2 | 13.85
WDZB1-BYJ-4 | 4.8 | 18.1
WDZB1-BYJ-6 | 5.4 | 22.9
WDZB1-BYJ-10 | 6.8 | 36.32
WDZB1-BYJ-16 | 8 | 50.27
WDZB1-BYJ-25 | 9.8 | 75.43
WDZB1-BYJ-35 | 11 | 95.03
WDZB1-BYJ-50 | 13 | 132.73
WDZB1-BYJ-70 | 15 | 176.71
WDZB1-BYJ-95 | 17 | 226.98
WDZB1-BYJ-120 | 19 | 283.53
WDZB1-BYJ-150 | 21 | 346.36
WDZB1-BYJ-185 | 23.5 | 433.74
WDZB1-BYJ-240 | 26.5 | 551.55
WDZB1-BYJ-300 | 29.5 | 683.49
WDZB1-BYJ-400 | 33.5 | 881.41
WDZB1-BYJR 450/750V 铜芯交联聚烯烃绝缘无卤低烟阻燃B1级软电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB1-BYJR-2.5 | 4.1 | 13.2
WDZB1-BYJR-4 | 4.8 | 18.1
WDZB1-BYJR-6 | 5.3 | 22.06
WDZB1-BYJR-10 | 7.3 | 41.85
WDZB1-BYJR-16 | 8.6 | 58.09
WDZB1-BYJR-25 | 10.2 | 81.71
WDZB1-BYJR-35 | 11.7 | 107.51
WDZB1-BYJR-50 | 13.9 | 151.75
WDZB1-BYJR-70 | 16 | 201.06
WDZB1-BYJR-95 | 18.2 | 260.16
WDZB1-BYJR-120 | 20.2 | 320.47
WDZB1-BYJR-150 | 22.5 | 397.61
WDZB1-BYJR-185 | 24.9 | 486.95
WDZB1-BYJR-240 | 28.4 | 633.47
WDZB1-BYJR-300 | 31.2 | 764.54
WDZB1-BYJR-400 | 35.5 | 989.8
WDZB1-RYJ 300/500V 铜芯单芯软导体交联聚烯烃绝缘无卤低烟阻燃B1级电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB1-RYJ-0.5 | 2.5 | 4.91
WDZB1-RYJ-0.75 | 2.7 | 5.73
WDZB1-RYJ-1.0 | 2.8 | 6.16
WDZB1-RYJ 450/750V 铜芯单芯软导体交联聚烯烃绝缘无卤低烟阻燃B1级电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB1-RYJ-1.5 | 3.4 | 9.08
WDZB1-RYJ-2.5 | 4.1 | 13.2
WDZB1-RYJ-4 | 4.8 | 18.1
WDZB1-RYJ-6 | 5.3 | 22.06
WDZB1-RYJ-10 | 6.8 | 36.32
WDZB1-RYJ-16 | 8.1 | 51.53
WDZB1-RYJ-25 | 10.2 | 81.71
WDZB1-RYJ-35 | 11.7 | 107.51
WDZB1-RYJ-50 | 13.9 | 151.75
WDZB1-RYJ-70 | 16 | 201.06
WDZB1-RYJ-95 | 18.2 | 260.16
WDZB1-RYJ-120 | 20.2 | 320.47
WDZB1-RYJ-150 | 22.5 | 397.61
WDZB1-RYJ-185 | 24.9 | 486.95
WDZB1-RYJ-240 | 28.4 | 633.47
WDZB1-RYJS 300/300V 铜芯交联聚烯烃绝缘绞型连接用无卤低烟阻燃B1级软电线
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZB1-RYJS-2*0.3 | 4.4 | 15.21
WDZB1-RYJS-2*0.4 | 4.8 | 18.1
WDZB1-RYJS-2*0.5 | 6 | 28.27
WDZB1-RYJS-2*0.75 | 6.2 | 30.19
WDZB1-RYJS-2*1.0 | 6.6 | 34.21
WDZB1-RYJS-2*1.5 | 7.2 | 40.72
WDZB1-RYJS-2*2.5 | 8.2 | 52.81
WDZB1-RYJS-2*4 | 9.5 | 70.88
WDZB1-RYJS-2*6 | 11.6 | 105.68
YJV/ZC-YJV/ZD-YJV 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚氯乙烯护套电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
YJV-1*1.5 | 5.6 | 24.63
YJV-1*2.5 | 6 | 28.27
YJV-1*4 | 6.4 | 32.17
YJV-1*6 | 6.9 | 37.39
YJV-1*10 | 8.1 | 51.53
YJV-1*16 | 9.1 | 65.04
YJV-1*25 | 10.8 | 91.61
YJV-1*35 | 11.7 | 107.51
YJV-1*50 | 13.1 | 134.78
YJV-1*70 | 15 | 176.71
YJV-1*95 | 17 | 226.98
YJV-1*120 | 18.6 | 271.72
YJV-1*150 | 20.5 | 330.06
YJV-1*185 | 22.9 | 411.87
YJV-1*240 | 25.8 | 522.79
YJV-1*300 | 28.3 | 629.02
YJV-1*400 | 31.6 | 784.27
YJV-1*500 | 35.2 | 973.14
YJV-2*1.5 | 9.4 | 69.4
YJV-2*2.5 | 10.1 | 80.12
YJV-2*4 | 11.1 | 96.77
YJV-2*6 | 12.1 | 114.99
YJV-2*10 | 14.4 | 162.86
YJV-2*16 | 16.4 | 211.24
YJV-2*25 | 20 | 314.16
YJV-2*35 | 21.8 | 373.25
YJV-2*50 | 22.2 | 387.08
YJV-2*70 | 25 | 490.87
YJV-2*95 | 27.5 | 593.96
YJV-2*120 | 30.2 | 716.31
YJV-2*150 | 33.2 | 865.7
YJV-2*185 | 36.6 | 1052.09
YJV-2*240 | 40.5 | 1288.25
YJV-2*300 | 44 | 1520.53
YJV-2*400 | 49.6 | 1932.21
YJV-3*1.5 | 9.8 | 75.43
YJV-3*2.5 | 10.6 | 88.25
YJV-3*4 | 11.7 | 107.51
YJV-3*6 | 12.7 | 126.68
YJV-3*10 | 15.3 | 183.85
YJV-3*16 | 17.4 | 237.79
YJV-3*25 | 21.2 | 352.99
YJV-3*35 | 23.2 | 422.73
YJV-3*50 | 29 | 660.52
YJV-3*70 | 33.4 | 876.16
YJV-3*95 | 37.3 | 1092.72
YJV-3*120 | 41 | 1320.25
YJV-3*150 | 45.1 | 1597.51
YJV-3*185 | 50 | 1963.5
YJV-3*240 | 56.2 | 2480.63
YJV-3*300 | 62.2 | 3038.58
YJV-3*400 | 69 | 3739.28
YJV-4*1.5 | 10.5 | 86.59
YJV-4*2.5 | 11.5 | 103.87
YJV-4*4 | 12.6 | 124.69
YJV-4*6 | 13.8 | 149.57
YJV-4*10 | 16.6 | 216.42
YJV-4*16 | 19.1 | 286.52
YJV-4*25 | 23.3 | 426.38
YJV-4*35 | 25.5 | 510.71
YJV-4*50 | 31.8 | 794.23
YJV-4*70 | 36.7 | 1057.84
YJV-4*95 | 41.2 | 1333.17
YJV-4*120 | 45.4 | 1618.83
YJV-4*150 | 49.8 | 1947.82
YJV-4*185 | 55.5 | 2419.22
YJV-4*240 | 62.4 | 3058.15
YJV-4*300 | 69 | 3739.28
YJV-4*400 | 76.5 | 4596.35
YJV-5*1.5 | 11.3 | 100.29
YJV-5*2.5 | 12.3 | 118.82
YJV-5*4 | 13.6 | 145.27
YJV-5*6 | 15 | 176.71
YJV-5*10 | 18.1 | 257.3
YJV-5*16 | 20.8 | 339.79
YJV-5*25 | 25.5 | 510.71
YJV-5*35 | 28 | 615.75
YJV-5*50 | 35 | 962.11
YJV-5*70 | 40.3 | 1275.56
YJV-5*95 | 45.5 | 1625.97
YJV-5*120 | 50 | 1963.5
YJV-5*150 | 55 | 2375.83
YJV-5*185 | 61.3 | 2951.28
YJV-5*240 | 69 | 3739.28
YJV-5*300 | 76.3 | 4572.34
YJV-5*400 | 84.8 | 5647.83
YJV-3*2.5+1*1.5 | 11.2 | 98.52
YJV-3*4+1*2.5 | 12.3 | 118.82
YJV-3*6+1*4 | 13.5 | 143.14
YJV-3*10+1*6 | 16 | 201.06
YJV-3*16+1*10 | 18.5 | 268.8
YJV-3*25+1*16 | 22.3 | 390.57
YJV-3*35+1*16 | 24 | 452.39
YJV-3*50+1*25 | 30.2 | 716.31
YJV-3*70+1*35 | 34.5 | 934.82
YJV-3*95+1*50 | 39 | 1194.59
YJV-3*120+1*70 | 43.2 | 1465.74
YJV-3*120+1*95 | 44.3 | 1541.34
YJV-3*150+1*70 | 46.5 | 1698.23
YJV-3*150+1*95 | 47.8 | 1794.51
YJV-3*185+1*95 | 52 | 2123.72
YJV-3*185+1*120 | 53 | 2206.18
YJV-3*240+1*120 | 58.2 | 2660.33
YJV-3*300+1*150 | 64.3 | 3247.22
YJV-3*400+1*185 | 71.2 | 3981.53
YJV-3*2.5+2*1.5 | 12 | 113.1
YJV-3*4+2*2.5 | 13.1 | 134.78
YJV-3*6+2*4 | 14.4 | 162.86
YJV-3*10+2*6 | 16.9 | 224.32
YJV-3*16+2*10 | 19.7 | 304.81
YJV-3*25+2*16 | 23.7 | 441.15
YJV-3*35+2*16 | 25.2 | 498.76
YJV-3*50+2*25 | 32.2 | 814.33
YJV-3*70+2*35 | 36.6 | 1052.09
YJV-3*95+2*50 | 41.3 | 1339.65
YJV-3*120+2*70 | 46.2 | 1676.39
YJV-3*150+2*70 | 49.1 | 1893.45
YJV-3*150+2*95 | 51.2 | 2058.87
YJV-3*185+2*95 | 55 | 2375.83
YJV-3*240+2*120 | 61.5 | 2970.57
YJV-3*300+2*150 | 67.8 | 3610.35
YJV-3*400+2*185 | 75.4 | 4465.11
YJV-4*2.5+1*1.5 | 12.1 | 114.99
YJV-4*4+1*2.5 | 13.4 | 141.03
YJV-4*6+1*4 | 14.7 | 169.72
YJV-4*10+1*6 | 17.5 | 240.53
YJV-4*16+1*10 | 20.3 | 323.65
YJV-4*25+1*16 | 24.6 | 475.29
YJV-4*35+1*16 | 26.6 | 555.72
YJV-4*50+1*25 | 33.4 | 876.16
YJV-4*70+1*35 | 38.6 | 1170.21
YJV-4*95+1*50 | 43.3 | 1472.54
YJV-4*120+1*70 | 48.2 | 1824.67
YJV-4*120+1*95 | 49.1 | 1893.45
YJV-4*150+1*70 | 52.1 | 2131.89
YJV-4*150+1*95 | 53 | 2206.18
YJV-4*185+1*95 | 58.2 | 2660.33
YJV-4*240+1*120 | 65.2 | 3338.76
YJV-4*300+1*150 | 72.1 | 4082.82
YJV-4*400+1*185 | 80 | 5026.55
ZA-YJV/ZB-YJV 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚氯乙烯护套电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
ZA-YJV-1*1.5 | 5.6 | 24.63
ZA-YJV-1*2.5 | 6 | 28.27
ZA-YJV-1*4 | 6.4 | 32.17
ZA-YJV-1*6 | 6.9 | 37.39
ZA-YJV-1*10 | 8.1 | 51.53
ZA-YJV-1*16 | 9.1 | 65.04
ZA-YJV-1*25 | 10.8 | 91.61
ZA-YJV-1*35 | 11.7 | 107.51
ZA-YJV-1*50 | 13.1 | 134.78
ZA-YJV-1*70 | 15 | 176.71
ZA-YJV-1*95 | 17 | 226.98
ZA-YJV-1*120 | 18.6 | 271.72
ZA-YJV-1*150 | 20.5 | 330.06
ZA-YJV-1*185 | 22.9 | 411.87
ZA-YJV-1*240 | 25.8 | 522.79
ZA-YJV-1*300 | 28.3 | 629.02
ZA-YJV-1*400 | 31.6 | 784.27
ZA-YJV-1*500 | 35.2 | 973.14
ZA-YJV-2*1.5 | 9.4 | 69.4
ZA-YJV-2*2.5 | 10.1 | 80.12
ZA-YJV-2*4 | 11.1 | 96.77
ZA-YJV-2*6 | 12.1 | 114.99
ZA-YJV-2*10 | 14.4 | 162.86
ZA-YJV-2*16 | 16.4 | 211.24
ZA-YJV-2*25 | 20 | 314.16
ZA-YJV-2*35 | 21.8 | 373.25
ZA-YJV-2*50 | 22.2 | 387.08
ZA-YJV-2*70 | 25 | 490.87
ZA-YJV-2*95 | 27.5 | 593.96
ZA-YJV-2*120 | 30.2 | 716.31
ZA-YJV-2*150 | 33.2 | 865.7
ZA-YJV-2*185 | 36.6 | 1052.09
ZA-YJV-2*240 | 40.5 | 1288.25
ZA-YJV-2*300 | 44 | 1520.53
ZA-YJV-2*400 | 49.6 | 1932.21
ZA-YJV-3*1.5 | 9.8 | 75.43
ZA-YJV-3*2.5 | 10.6 | 88.25
ZA-YJV-3*4 | 11.7 | 107.51
ZA-YJV-3*6 | 12.7 | 126.68
ZA-YJV-3*10 | 15.3 | 183.85
ZA-YJV-3*16 | 17.4 | 237.79
ZA-YJV-3*25 | 21.2 | 352.99
ZA-YJV-3*35 | 23.2 | 422.73
ZA-YJV-3*50 | 29 | 660.52
ZA-YJV-3*70 | 33.4 | 876.16
ZA-YJV-3*95 | 37.3 | 1092.72
ZA-YJV-3*120 | 41 | 1320.25
ZA-YJV-3*150 | 45.1 | 1597.51
ZA-YJV-3*185 | 50 | 1963.5
ZA-YJV-3*240 | 56.2 | 2480.63
ZA-YJV-3*300 | 62.2 | 3038.58
ZA-YJV-3*400 | 69 | 3739.28
ZA-YJV-4*1.5 | 10.5 | 86.59
ZA-YJV-4*2.5 | 11.5 | 103.87
ZA-YJV-4*4 | 12.6 | 124.69
ZA-YJV-4*6 | 13.8 | 149.57
ZA-YJV-4*10 | 16.6 | 216.42
ZA-YJV-4*16 | 19.1 | 286.52
ZA-YJV-4*25 | 23.3 | 426.38
ZA-YJV-4*35 | 25.5 | 510.71
ZA-YJV-4*50 | 31.8 | 794.23
ZA-YJV-4*70 | 36.7 | 1057.84
ZA-YJV-4*95 | 41.2 | 1333.17
ZA-YJV-4*120 | 45.4 | 1618.83
ZA-YJV-4*150 | 49.8 | 1947.82
ZA-YJV-4*185 | 55.5 | 2419.22
ZA-YJV-4*240 | 62.4 | 3058.15
ZA-YJV-4*300 | 69 | 3739.28
ZA-YJV-4*400 | 76.5 | 4596.35
ZA-YJV-5*1.5 | 11.3 | 100.29
ZA-YJV-5*2.5 | 12.3 | 118.82
ZA-YJV-5*4 | 13.6 | 145.27
ZA-YJV-5*6 | 15 | 176.71
ZA-YJV-5*10 | 18.1 | 257.3
ZA-YJV-5*16 | 20.8 | 339.79
ZA-YJV-5*25 | 25.5 | 510.71
ZA-YJV-5*35 | 28 | 615.75
ZA-YJV-5*50 | 35 | 962.11
ZA-YJV-5*70 | 40.3 | 1275.56
ZA-YJV-5*95 | 45.5 | 1625.97
ZA-YJV-5*120 | 50 | 1963.5
ZA-YJV-5*150 | 55 | 2375.83
ZA-YJV-5*185 | 61.3 | 2951.28
ZA-YJV-5*240 | 69 | 3739.28
ZA-YJV-5*300 | 76.3 | 4572.34
ZA-YJV-5*400 | 84.8 | 5647.83
ZA-YJV-3*2.5+1*1.5 | 11.2 | 98.52
ZA-YJV-3*4+1*2.5 | 12.3 | 118.82
ZA-YJV-3*6+1*4 | 13.5 | 143.14
ZA-YJV-3*10+1*6 | 16 | 201.06
ZA-YJV-3*16+1*10 | 18.5 | 268.8
ZA-YJV-3*25+1*16 | 22.3 | 390.57
ZA-YJV-3*35+1*16 | 24 | 452.39
ZA-YJV-3*50+1*25 | 30.2 | 716.31
ZA-YJV-3*70+1*35 | 34.5 | 934.82
ZA-YJV-3*95+1*50 | 39 | 1194.59
ZA-YJV-3*120+1*70 | 43.2 | 1465.74
ZA-YJV-3*120+1*95 | 44.3 | 1541.34
ZA-YJV-3*150+1*70 | 46.5 | 1698.23
ZA-YJV-3*150+1*95 | 47.8 | 1794.51
ZA-YJV-3*185+1*95 | 52 | 2123.72
ZA-YJV-3*185+1*120 | 53 | 2206.18
ZA-YJV-3*240+1*120 | 58.2 | 2660.33
ZA-YJV-3*300+1*150 | 64.3 | 3247.22
ZA-YJV-3*400+1*185 | 71.2 | 3981.53
ZA-YJV-3*2.5+2*1.5 | 12 | 113.1
ZA-YJV-3*4+2*2.5 | 13.1 | 134.78
ZA-YJV-3*6+2*4 | 14.4 | 162.86
ZA-YJV-3*10+2*6 | 16.9 | 224.32
ZA-YJV-3*16+2*10 | 19.7 | 304.81
ZA-YJV-3*25+2*16 | 23.7 | 441.15
ZA-YJV-3*35+2*16 | 25.2 | 498.76
ZA-YJV-3*50+2*25 | 32.2 | 814.33
ZA-YJV-3*70+2*35 | 36.6 | 1052.09
ZA-YJV-3*95+2*50 | 41.3 | 1339.65
ZA-YJV-3*120+2*70 | 46.2 | 1676.39
ZA-YJV-3*150+2*70 | 49.1 | 1893.45
ZA-YJV-3*150+2*95 | 51.2 | 2058.87
ZA-YJV-3*185+2*95 | 55 | 2375.83
ZA-YJV-3*240+2*120 | 61.5 | 2970.57
ZA-YJV-3*300+2*150 | 67.8 | 3610.35
ZA-YJV-3*400+2*185 | 75.4 | 4465.11
ZA-YJV-4*2.5+1*1.5 | 12.1 | 114.99
ZA-YJV-4*4+1*2.5 | 13.4 | 141.03
ZA-YJV-4*6+1*4 | 14.7 | 169.72
ZA-YJV-4*10+1*6 | 17.5 | 240.53
ZA-YJV-4*16+1*10 | 20.3 | 323.65
ZA-YJV-4*25+1*16 | 24.6 | 475.29
ZA-YJV-4*35+1*16 | 26.6 | 555.72
ZA-YJV-4*50+1*25 | 33.4 | 876.16
ZA-YJV-4*70+1*35 | 38.6 | 1170.21
ZA-YJV-4*95+1*50 | 43.3 | 1472.54
ZA-YJV-4*120+1*70 | 48.2 | 1824.67
ZA-YJV-4*120+1*95 | 49.1 | 1893.45
ZA-YJV-4*150+1*70 | 52.1 | 2131.89
ZA-YJV-4*150+1*95 | 53 | 2206.18
ZA-YJV-4*185+1*95 | 58.2 | 2660.33
ZA-YJV-4*240+1*120 | 65.2 | 3338.76
ZA-YJV-4*300+1*150 | 72.1 | 4082.82
ZA-YJV-4*400+1*185 | 80 | 5026.55
WDZA-YJY/WDZB-YJY/WDZ-YJY/WDZC-YJY/WDZD-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚氯乙烯护套无卤低烟阻燃电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZ-YJY-1*1.5 | 8 | 50.27
WDZ-YJY-1*2.5 | 8.4 | 55.42
WDZ-YJY-1*4 | 8.8 | 60.82
WDZ-YJY-1*6 | 9.3 | 67.93
WDZ-YJY-1*10 | 10.5 | 86.59
WDZ-YJY-1*16 | 11.5 | 103.87
WDZ-YJY-1*25 | 13.2 | 136.85
WDZ-YJY-1*35 | 14.1 | 156.15
WDZ-YJY-1*50 | 15.5 | 188.69
WDZ-YJY-1*70 | 17.4 | 237.79
WDZ-YJY-1*95 | 19.4 | 295.59
WDZ-YJY-1*120 | 21 | 346.36
WDZ-YJY-1*150 | 22.9 | 411.87
WDZ-YJY-1*185 | 25.3 | 502.73
WDZ-YJY-1*240 | 28.2 | 624.58
WDZ-YJY-1*300 | 30.7 | 740.23
WDZ-YJY-1*400 | 34.4 | 929.41
WDZ-YJY-1*500 | 38 | 1134.11
WDZ-YJY-2*1.5 | 11.8 | 109.36
WDZ-YJY-2*2.5 | 12.6 | 124.69
WDZ-YJY-2*4 | 13.5 | 143.14
WDZ-YJY-2*6 | 14.5 | 165.13
WDZ-YJY-2*10 | 17.2 | 232.35
WDZ-YJY-2*16 | 19.2 | 289.53
WDZ-YJY-2*25 | 23.1 | 419.1
WDZ-YJY-2*35 | 25 | 490.87
WDZ-YJY-2*50 | 24.6 | 475.29
WDZ-YJY-2*70 | 27.3 | 585.35
WDZ-YJY-2*95 | 30.3 | 721.07
WDZ-YJY-2*120 | 33 | 855.3
WDZ-YJY-2*150 | 36.1 | 1023.54
WDZ-YJY-2*185 | 39.8 | 1244.1
WDZ-YJY-2*240 | 43.7 | 1499.87
WDZ-YJY-2*300 | 47.6 | 1779.52
WDZ-YJY-2*400 | 53.2 | 2222.87
WDZ-YJY-3*1.5 | 12.2 | 116.9
WDZ-YJY-3*2.5 | 13.1 | 134.78
WDZ-YJY-3*4 | 14.1 | 156.15
WDZ-YJY-3*6 | 15.2 | 181.46
WDZ-YJY-3*10 | 18.1 | 257.3
WDZ-YJY-3*16 | 20.2 | 320.47
WDZ-YJY-3*25 | 24.4 | 467.59
WDZ-YJY-3*35 | 26.4 | 547.39
WDZ-YJY-3*50 | 31.3 | 769.45
WDZ-YJY-3*70 | 36.2 | 1029.22
WDZ-YJY-3*95 | 40.1 | 1262.93
WDZ-YJY-3*120 | 43.8 | 1506.74
WDZ-YJY-3*150 | 48.3 | 1832.25
WDZ-YJY-3*185 | 50 | 1963.5
WDZ-YJY-3*240 | 56.2 | 2480.63
WDZ-YJY-3*300 | 62.2 | 3038.58
WDZ-YJY-3*400 | 72.5 | 4128.25
WDZ-YJY-4*1.5 | 13 | 132.73
WDZ-YJY-4*2.5 | 13.9 | 151.75
WDZ-YJY-4*4 | 15 | 176.71
WDZ-YJY-4*6 | 16.2 | 206.12
WDZ-YJY-4*10 | 19.4 | 295.59
WDZ-YJY-4*16 | 21.9 | 376.68
WDZ-YJY-4*25 | 26.4 | 547.39
WDZ-YJY-4*35 | 28.7 | 646.92
WDZ-YJY-4*50 | 34.2 | 918.63
WDZ-YJY-4*70 | 39.5 | 1225.42
WDZ-YJY-4*95 | 44 | 1520.53
WDZ-YJY-4*120 | 48.6 | 1855.08
WDZ-YJY-4*150 | 53 | 2206.18
WDZ-YJY-4*185 | 58.7 | 2706.24
WDZ-YJY-4*240 | 66 | 3421.19
WDZ-YJY-4*300 | 72.6 | 4139.65
WDZ-YJY-4*400 | 80.5 | 5089.58
WDZ-YJY-5*1.5 | 13.8 | 149.57
WDZ-YJY-5*2.5 | 14.8 | 172.03
WDZ-YJY-5*4 | 16 | 201.06
WDZ-YJY-5*6 | 17.4 | 237.79
WDZ-YJY-5*10 | 21 | 346.36
WDZ-YJY-5*16 | 23.6 | 437.44
WDZ-YJY-5*25 | 28.7 | 646.92
WDZ-YJY-5*35 | 31.2 | 764.54
WDZ-YJY-5*50 | 37.7 | 1116.28
WDZ-YJY-5*70 | 43.1 | 1458.96
WDZ-YJY-5*95 | 48.7 | 1862.72
WDZ-YJY-5*120 | 53.2 | 2222.87
WDZ-YJY-5*150 | 58.2 | 2660.33
WDZ-YJY-5*185 | 65 | 3318.31
WDZ-YJY-5*240 | 72.6 | 4139.65
WDZ-YJY-5*300 | 80.3 | 5064.32
WDZ-YJY-5*400 | 88.8 | 6193.21
WDZ-YJY-3*2.5+1*1.5 | 13.7 | 147.41
WDZ-YJY-3*4+1*2.5 | 14.7 | 169.72
WDZ-YJY-3*6+1*4 | 15.9 | 198.56
WDZ-YJY-3*10+1*6 | 18.7 | 274.65
WDZ-YJY-3*16+1*10 | 21.2 | 352.99
WDZ-YJY-3*25+1*16 | 25.4 | 506.71
WDZ-YJY-3*35+1*16 | 27.1 | 576.8
WDZ-YJY-3*50+1*25 | 32.6 | 834.69
WDZ-YJY-3*70+1*35 | 37.3 | 1092.72
WDZ-YJY-3*95+1*50 | 41.7 | 1365.72
WDZ-YJY-3*120+1*70 | 46 | 1661.9
WDZ-YJY-3*120+1*95 | 47.1 | 1742.34
WDZ-YJY-3*150+1*70 | 49.7 | 1940
WDZ-YJY-3*150+1*95 | 51 | 2042.82
WDZ-YJY-3*185+1*95 | 55.1 | 2384.48
WDZ-YJY-3*185+1*120 | 56.1 | 2471.81
WDZ-YJY-3*240+1*120 | 61.8 | 2999.62
WDZ-YJY-3*300+1*150 | 67.9 | 3621.01
WDZ-YJY-3*400+1*185 | 74.8 | 4394.33
WDZ-YJY-3*2.5+2*1.5 | 14.4 | 162.86
WDZ-YJY-3*4+2*2.5 | 15.5 | 188.69
WDZ-YJY-3*6+2*4 | 16.9 | 224.32
WDZ-YJY-3*10+2*6 | 19.7 | 304.81
WDZ-YJY-3*16+2*10 | 22.5 | 397.61
WDZ-YJY-3*25+2*16 | 26.9 | 568.32
WDZ-YJY-3*35+2*16 | 28.4 | 633.47
WDZ-YJY-3*50+2*25 | 34.6 | 940.25
WDZ-YJY-3*70+2*35 | 39.4 | 1219.22
WDZ-YJY-3*95+2*50 | 44.1 | 1527.45
WDZ-YJY-3*120+2*70 | 49.4 | 1916.65
WDZ-YJY-3*150+2*70 | 52.3 | 2148.29
WDZ-YJY-3*150+2*95 | 54.4 | 2324.28
WDZ-YJY-3*185+2*95 | 58.2 | 2660.33
WDZ-YJY-3*240+2*120 | 65.1 | 3328.53
WDZ-YJY-3*300+2*150 | 71.4 | 4003.93
WDZ-YJY-3*400+2*185 | 79.4 | 4951.43
WDZ-YJY-4*2.5+1*1.5 | 14.6 | 167.42
WDZ-YJY-4*4+1*2.5 | 15.8 | 196.07
WDZ-YJY-4*6+1*4 | 17.1 | 229.66
WDZ-YJY-4*10+1*6 | 20.3 | 323.65
WDZ-YJY-4*16+1*10 | 23.1 | 419.1
WDZ-YJY-4*25+1*16 | 27.8 | 606.99
WDZ-YJY-4*35+1*16 | 29.8 | 697.46
WDZ-YJY-4*50+1*25 | 36.2 | 1029.22
WDZ-YJY-4*70+1*35 | 41.4 | 1346.14
WDZ-YJY-4*95+1*50 | 46.1 | 1669.14
WDZ-YJY-4*120+1*70 | 51.4 | 2074.99
WDZ-YJY-4*120+1*95 | 52.3 | 2148.29
WDZ-YJY-4*150+1*70 | 55.3 | 2401.82
WDZ-YJY-4*150+1*95 | 56.2 | 2480.63
WDZ-YJY-4*185+1*95 | 61.8 | 2999.62
WDZ-YJY-4*240+1*120 | 68.9 | 3728.45
WDZ-YJY-4*300+1*150 | 75.7 | 4500.72
WDZ-YJY-4*400+1*185 | 84 | 5541.77
NH-YJV/ZCN-YJV/ZDN-YJV 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚氯乙烯护套耐火电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
NH-YJV-1*1.5 | 6.3 | 31.17
NH-YJV-1*2.5 | 6.7 | 35.26
NH-YJV-1*4 | 7.1 | 39.59
NH-YJV-1*6 | 7.6 | 45.36
NH-YJV-1*10 | 8.8 | 60.82
NH-YJV-1*16 | 9.8 | 75.43
NH-YJV-1*25 | 11.5 | 103.87
NH-YJV-1*35 | 12.4 | 120.76
NH-YJV-1*50 | 13.8 | 149.57
NH-YJV-1*70 | 15.7 | 193.59
NH-YJV-1*95 | 17.7 | 246.06
NH-YJV-1*120 | 19.3 | 292.55
NH-YJV-1*150 | 21.2 | 352.99
NH-YJV-1*185 | 23.6 | 437.44
NH-YJV-1*240 | 26.5 | 551.55
NH-YJV-1*300 | 29 | 660.52
NH-YJV-1*400 | 32.3 | 819.4
NH-YJV-1*500 | 35.9 | 1012.23
NH-YJV-2*1.5 | 10.7 | 89.92
NH-YJV-2*2.5 | 11.4 | 102.07
NH-YJV-2*4 | 12.4 | 120.76
NH-YJV-2*6 | 13.4 | 141.03
NH-YJV-2*10 | 15.7 | 193.59
NH-YJV-2*16 | 17.7 | 246.06
NH-YJV-2*25 | 21.3 | 356.33
NH-YJV-2*35 | 23.1 | 419.1
NH-YJV-2*50 | 23.5 | 433.74
NH-YJV-2*70 | 26.3 | 543.25
NH-YJV-2*95 | 28.8 | 651.44
NH-YJV-2*120 | 31.5 | 779.31
NH-YJV-2*150 | 34.5 | 934.82
NH-YJV-2*185 | 37.9 | 1128.15
NH-YJV-2*240 | 41.8 | 1372.28
NH-YJV-2*300 | 45.3 | 1611.71
NH-YJV-2*400 | 50.9 | 2034.82
NH-YJV-3*1.5 | 11.2 | 98.52
NH-YJV-3*2.5 | 12 | 113.1
NH-YJV-3*4 | 13.1 | 134.78
NH-YJV-3*6 | 14.1 | 156.15
NH-YJV-3*10 | 16.7 | 219.04
NH-YJV-3*16 | 18.8 | 277.59
NH-YJV-3*25 | 22.6 | 401.15
NH-YJV-3*35 | 24.6 | 475.29
NH-YJV-3*50 | 30.4 | 725.83
NH-YJV-3*70 | 34.8 | 951.15
NH-YJV-3*95 | 38.7 | 1176.28
NH-YJV-3*120 | 42.4 | 1411.96
NH-YJV-3*150 | 46.5 | 1698.23
NH-YJV-3*185 | 51.4 | 2074.99
NH-YJV-3*240 | 57.6 | 2605.76
NH-YJV-3*300 | 63.6 | 3176.9
NH-YJV-3*400 | 70.4 | 3892.56
NH-YJV-4*1.5 | 12.1 | 114.99
NH-YJV-4*2.5 | 13.1 | 134.78
NH-YJV-4*4 | 14.2 | 158.37
NH-YJV-4*6 | 15.4 | 186.27
NH-YJV-4*10 | 18.2 | 260.16
NH-YJV-4*16 | 20.7 | 336.54
NH-YJV-4*25 | 24.9 | 486.95
NH-YJV-4*35 | 27.1 | 576.8
NH-YJV-4*50 | 33.4 | 876.16
NH-YJV-4*70 | 38.3 | 1152.09
NH-YJV-4*95 | 42.8 | 1438.72
NH-YJV-4*120 | 47 | 1734.94
NH-YJV-4*150 | 51.4 | 2074.99
NH-YJV-4*185 | 57.1 | 2560.72
NH-YJV-4*240 | 64 | 3216.99
NH-YJV-4*300 | 70.6 | 3914.71
NH-YJV-4*400 | 78.1 | 4790.62
NH-YJV-5*1.5 | 13.1 | 134.78
NH-YJV-5*2.5 | 14.1 | 156.15
NH-YJV-5*4 | 15.4 | 186.27
NH-YJV-5*6 | 16.8 | 221.67
NH-YJV-5*10 | 19.9 | 311.03
NH-YJV-5*16 | 22.6 | 401.15
NH-YJV-5*25 | 27.3 | 585.35
NH-YJV-5*35 | 29.8 | 697.46
NH-YJV-5*50 | 36.8 | 1063.62
NH-YJV-5*70 | 42.1 | 1392.05
NH-YJV-5*95 | 47.3 | 1757.16
NH-YJV-5*120 | 51.8 | 2107.41
NH-YJV-5*150 | 56.8 | 2533.88
NH-YJV-5*185 | 63.1 | 3127.15
NH-YJV-5*240 | 70.8 | 3936.92
NH-YJV-5*300 | 78.1 | 4790.62
NH-YJV-5*400 | 86.6 | 5890.14
NH-YJV-3*2.5+1*1.5 | 12.8 | 128.68
NH-YJV-3*4+1*2.5 | 13.9 | 151.75
NH-YJV-3*6+1*4 | 15.1 | 179.08
NH-YJV-3*10+1*6 | 17.6 | 243.28
NH-YJV-3*16+1*10 | 20.1 | 317.31
NH-YJV-3*25+1*16 | 23.9 | 448.63
NH-YJV-3*35+1*16 | 25.6 | 514.72
NH-YJV-3*50+1*25 | 31.8 | 794.23
NH-YJV-3*70+1*35 | 36.1 | 1023.54
NH-YJV-3*95+1*50 | 40.6 | 1294.62
NH-YJV-3*120+1*70 | 44.8 | 1576.33
NH-YJV-3*120+1*95 | 45.9 | 1654.68
NH-YJV-3*150+1*70 | 48.1 | 1817.11
NH-YJV-3*150+1*95 | 49.4 | 1916.65
NH-YJV-3*185+1*95 | 53.6 | 2256.42
NH-YJV-3*185+1*120 | 54.6 | 2341.4
NH-YJV-3*240+1*120 | 59.8 | 2808.62
NH-YJV-3*300+1*150 | 65.9 | 3410.83
NH-YJV-3*400+1*185 | 72.8 | 4162.48
NH-YJV-3*2.5+2*1.5 | 13.8 | 149.57
NH-YJV-3*4+2*2.5 | 14.9 | 174.37
NH-YJV-3*6+2*4 | 16.2 | 206.12
NH-YJV-3*10+2*6 | 18.7 | 274.65
NH-YJV-3*16+2*10 | 21.5 | 363.05
NH-YJV-3*25+2*16 | 25.5 | 510.71
NH-YJV-3*35+2*16 | 27 | 572.56
NH-YJV-3*50+2*25 | 34 | 907.92
NH-YJV-3*70+2*35 | 38.4 | 1158.12
NH-YJV-3*95+2*50 | 43.1 | 1458.96
NH-YJV-3*120+2*70 | 48 | 1809.56
NH-YJV-3*150+2*70 | 50.9 | 2034.82
NH-YJV-3*150+2*95 | 53 | 2206.18
NH-YJV-3*185+2*95 | 56.8 | 2533.88
NH-YJV-3*240+2*120 | 63.3 | 3147
NH-YJV-3*300+2*150 | 69.6 | 3804.59
NH-YJV-3*400+2*185 | 77.2 | 4680.85
NH-YJV-4*2.5+1*1.5 | 13.9 | 151.75
NH-YJV-4*4+1*2.5 | 15.2 | 181.46
NH-YJV-4*6+1*4 | 16.5 | 213.82
NH-YJV-4*10+1*6 | 19.3 | 292.55
NH-YJV-4*16+1*10 | 22.1 | 383.6
NH-YJV-4*25+1*16 | 26.4 | 547.39
NH-YJV-4*35+1*16 | 28.4 | 633.47
NH-YJV-4*50+1*25 | 35.2 | 973.14
NH-YJV-4*70+1*35 | 40.4 | 1281.9
NH-YJV-4*95+1*50 | 45.1 | 1597.51
NH-YJV-4*120+1*70 | 50 | 1963.5
NH-YJV-4*120+1*95 | 50.9 | 2034.82
NH-YJV-4*150+1*70 | 53.9 | 2281.75
NH-YJV-4*150+1*95 | 54.8 | 2358.58
NH-YJV-4*185+1*95 | 60 | 2827.43
NH-YJV-4*240+1*120 | 67 | 3525.65
NH-YJV-4*300+1*150 | 73.9 | 4289.22
NH-YJV-4*400+1*185 | 81.8 | 5255.29
ZAN-YJV/ZBN-YJV 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚氯乙烯护套耐火电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
ZAN-YJV-1*1.5 | 6.3 | 31.17
ZAN-YJV-1*2.5 | 6.7 | 35.26
ZAN-YJV-1*4 | 7.1 | 39.59
ZAN-YJV-1*6 | 7.6 | 45.36
ZAN-YJV-1*10 | 8.8 | 60.82
ZAN-YJV-1*16 | 9.8 | 75.43
ZAN-YJV-1*25 | 11.5 | 103.87
ZAN-YJV-1*35 | 12.4 | 120.76
ZAN-YJV-1*50 | 13.8 | 149.57
ZAN-YJV-1*70 | 15.7 | 193.59
ZAN-YJV-1*95 | 17.7 | 246.06
ZAN-YJV-1*120 | 19.3 | 292.55
ZAN-YJV-1*150 | 21.2 | 352.99
ZAN-YJV-1*185 | 23.6 | 437.44
ZAN-YJV-1*240 | 26.5 | 551.55
ZAN-YJV-1*300 | 29 | 660.52
ZAN-YJV-1*400 | 32.3 | 819.4
ZAN-YJV-1*500 | 35.9 | 1012.23
ZAN-YJV-2*1.5 | 10.7 | 89.92
ZAN-YJV-2*2.5 | 11.4 | 102.07
ZAN-YJV-2*4 | 12.4 | 120.76
ZAN-YJV-2*6 | 13.4 | 141.03
ZAN-YJV-2*10 | 15.7 | 193.59
ZAN-YJV-2*16 | 17.7 | 246.06
ZAN-YJV-2*25 | 21.3 | 356.33
ZAN-YJV-2*35 | 23.1 | 419.1
ZAN-YJV-2*50 | 23.5 | 433.74
ZAN-YJV-2*70 | 26.3 | 543.25
ZAN-YJV-2*95 | 28.8 | 651.44
ZAN-YJV-2*120 | 31.5 | 779.31
ZAN-YJV-2*150 | 34.5 | 934.82
ZAN-YJV-2*185 | 37.9 | 1128.15
ZAN-YJV-2*240 | 41.8 | 1372.28
ZAN-YJV-2*300 | 45.3 | 1611.71
ZAN-YJV-2*400 | 50.9 | 2034.82
ZAN-YJV-3*1.5 | 11.2 | 98.52
ZAN-YJV-3*2.5 | 12 | 113.1
ZAN-YJV-3*4 | 13.1 | 134.78
ZAN-YJV-3*6 | 14.1 | 156.15
ZAN-YJV-3*10 | 16.7 | 219.04
ZAN-YJV-3*16 | 18.8 | 277.59
ZAN-YJV-3*25 | 22.6 | 401.15
ZAN-YJV-3*35 | 24.6 | 475.29
ZAN-YJV-3*50 | 30.4 | 725.83
ZAN-YJV-3*70 | 34.8 | 951.15
ZAN-YJV-3*95 | 38.7 | 1176.28
ZAN-YJV-3*120 | 42.4 | 1411.96
ZAN-YJV-3*150 | 46.5 | 1698.23
ZAN-YJV-3*185 | 51.4 | 2074.99
ZAN-YJV-3*240 | 57.6 | 2605.76
ZAN-YJV-3*300 | 63.6 | 3176.9
ZAN-YJV-3*400 | 70.4 | 3892.56
ZAN-YJV-4*1.5 | 12.1 | 114.99
ZAN-YJV-4*2.5 | 13.1 | 134.78
ZAN-YJV-4*4 | 14.2 | 158.37
ZAN-YJV-4*6 | 15.4 | 186.27
ZAN-YJV-4*10 | 18.2 | 260.16
ZAN-YJV-4*16 | 20.7 | 336.54
ZAN-YJV-4*25 | 24.9 | 486.95
ZAN-YJV-4*35 | 27.1 | 576.8
ZAN-YJV-4*50 | 33.4 | 876.16
ZAN-YJV-4*70 | 38.3 | 1152.09
ZAN-YJV-4*95 | 42.8 | 1438.72
ZAN-YJV-4*120 | 47 | 1734.94
ZAN-YJV-4*150 | 51.4 | 2074.99
ZAN-YJV-4*185 | 57.1 | 2560.72
ZAN-YJV-4*240 | 64 | 3216.99
ZAN-YJV-4*300 | 70.6 | 3914.71
ZAN-YJV-4*400 | 78.1 | 4790.62
ZAN-YJV-5*1.5 | 13.1 | 134.78
ZAN-YJV-5*2.5 | 14.1 | 156.15
ZAN-YJV-5*4 | 15.4 | 186.27
ZAN-YJV-5*6 | 16.8 | 221.67
ZAN-YJV-5*10 | 19.9 | 311.03
ZAN-YJV-5*16 | 22.6 | 401.15
ZAN-YJV-5*25 | 27.3 | 585.35
ZAN-YJV-5*35 | 29.8 | 697.46
ZAN-YJV-5*50 | 36.8 | 1063.62
ZAN-YJV-5*70 | 42.1 | 1392.05
ZAN-YJV-5*95 | 47.3 | 1757.16
ZAN-YJV-5*120 | 51.8 | 2107.41
ZAN-YJV-5*150 | 56.8 | 2533.88
ZAN-YJV-5*185 | 63.1 | 3127.15
ZAN-YJV-5*240 | 70.8 | 3936.92
ZAN-YJV-5*300 | 78.1 | 4790.62
ZAN-YJV-5*400 | 86.6 | 5890.14
ZAN-YJV-3*2.5+1*1.5 | 12.8 | 128.68
ZAN-YJV-3*4+1*2.5 | 13.9 | 151.75
ZAN-YJV-3*6+1*4 | 15.1 | 179.08
ZAN-YJV-3*10+1*6 | 17.6 | 243.28
ZAN-YJV-3*16+1*10 | 20.1 | 317.31
ZAN-YJV-3*25+1*16 | 23.9 | 448.63
ZAN-YJV-3*35+1*16 | 25.6 | 514.72
ZAN-YJV-3*50+1*25 | 31.8 | 794.23
ZAN-YJV-3*70+1*35 | 36.1 | 1023.54
ZAN-YJV-3*95+1*50 | 40.6 | 1294.62
ZAN-YJV-3*120+1*70 | 44.8 | 1576.33
ZAN-YJV-3*120+1*95 | 45.9 | 1654.68
ZAN-YJV-3*150+1*70 | 48.1 | 1817.11
ZAN-YJV-3*150+1*95 | 49.4 | 1916.65
ZAN-YJV-3*185+1*95 | 53.6 | 2256.42
ZAN-YJV-3*185+1*120 | 54.6 | 2341.4
ZAN-YJV-3*240+1*120 | 59.8 | 2808.62
ZAN-YJV-3*300+1*150 | 65.9 | 3410.83
ZAN-YJV-3*400+1*185 | 72.8 | 4162.48
ZAN-YJV-3*2.5+2*1.5 | 13.8 | 149.57
ZAN-YJV-3*4+2*2.5 | 14.9 | 174.37
ZAN-YJV-3*6+2*4 | 16.2 | 206.12
ZAN-YJV-3*10+2*6 | 18.7 | 274.65
ZAN-YJV-3*16+2*10 | 21.5 | 363.05
ZAN-YJV-3*25+2*16 | 25.5 | 510.71
ZAN-YJV-3*35+2*16 | 27 | 572.56
ZAN-YJV-3*50+2*25 | 34 | 907.92
ZAN-YJV-3*70+2*35 | 38.4 | 1158.12
ZAN-YJV-3*95+2*50 | 43.1 | 1458.96
ZAN-YJV-3*120+2*70 | 48 | 1809.56
ZAN-YJV-3*150+2*70 | 50.9 | 2034.82
ZAN-YJV-3*150+2*95 | 53 | 2206.18
ZAN-YJV-3*185+2*95 | 56.8 | 2533.88
ZAN-YJV-3*240+2*120 | 63.3 | 3147
ZAN-YJV-3*300+2*150 | 69.6 | 3804.59
ZAN-YJV-3*400+2*185 | 77.2 | 4680.85
ZAN-YJV-4*2.5+1*1.5 | 13.9 | 151.75
ZAN-YJV-4*4+1*2.5 | 15.2 | 181.46
ZAN-YJV-4*6+1*4 | 16.5 | 213.82
ZAN-YJV-4*10+1*6 | 19.3 | 292.55
ZAN-YJV-4*16+1*10 | 22.1 | 383.6
ZAN-YJV-4*25+1*16 | 26.4 | 547.39
ZAN-YJV-4*35+1*16 | 28.4 | 633.47
ZAN-YJV-4*50+1*25 | 35.2 | 973.14
ZAN-YJV-4*70+1*35 | 40.4 | 1281.9
ZAN-YJV-4*95+1*50 | 45.1 | 1597.51
ZAN-YJV-4*120+1*70 | 50 | 1963.5
ZAN-YJV-4*120+1*95 | 50.9 | 2034.82
ZAN-YJV-4*150+1*70 | 53.9 | 2281.75
ZAN-YJV-4*150+1*95 | 54.8 | 2358.58
ZAN-YJV-4*185+1*95 | 60 | 2827.43
ZAN-YJV-4*240+1*120 | 67 | 3525.65
ZAN-YJV-4*300+1*150 | 73.9 | 4289.22
ZAN-YJV-4*400+1*185 | 81.8 | 5255.29
WDZAN-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘无卤低烟护套耐火电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZAN-YJY-1*1.5 | 8.7 | 59.45
WDZAN-YJY-1*2.5 | 9.1 | 65.04
WDZAN-YJY-1*4 | 9.5 | 70.88
WDZAN-YJY-1*6 | 10 | 78.54
WDZAN-YJY-1*10 | 11.2 | 98.52
WDZAN-YJY-1*16 | 12.2 | 116.9
WDZAN-YJY-1*25 | 13.9 | 151.75
WDZAN-YJY-1*35 | 14.8 | 172.03
WDZAN-YJY-1*50 | 16.2 | 206.12
WDZAN-YJY-1*70 | 18.1 | 257.3
WDZAN-YJY-1*95 | 20.1 | 317.31
WDZAN-YJY-1*120 | 21.7 | 369.84
WDZAN-YJY-1*150 | 23.6 | 437.44
WDZAN-YJY-1*185 | 26 | 530.93
WDZAN-YJY-1*240 | 28.9 | 655.97
WDZAN-YJY-1*300 | 31.4 | 774.37
WDZAN-YJY-1*400 | 35.1 | 967.62
WDZAN-YJY-1*500 | 38.7 | 1176.28
WDZAN-YJY-2*1.5 | 13.1 | 134.78
WDZAN-YJY-2*2.5 | 13.9 | 151.75
WDZAN-YJY-2*4 | 14.8 | 172.03
WDZAN-YJY-2*6 | 15.8 | 196.07
WDZAN-YJY-2*10 | 18.5 | 268.8
WDZAN-YJY-2*16 | 20.5 | 330.06
WDZAN-YJY-2*25 | 24.4 | 467.59
WDZAN-YJY-2*35 | 26.3 | 543.25
WDZAN-YJY-2*50 | 25.9 | 526.85
WDZAN-YJY-2*70 | 28.6 | 642.42
WDZAN-YJY-2*95 | 31.6 | 784.27
WDZAN-YJY-2*120 | 34.3 | 924.01
WDZAN-YJY-2*150 | 37.4 | 1098.58
WDZAN-YJY-2*185 | 41.1 | 1326.7
WDZAN-YJY-2*240 | 45 | 1590.43
WDZAN-YJY-2*300 | 48.9 | 1878.05
WDZAN-YJY-2*400 | 54.5 | 2332.83
WDZAN-YJY-3*1.5 | 13.6 | 145.27
WDZAN-YJY-3*2.5 | 14.5 | 165.13
WDZAN-YJY-3*4 | 15.5 | 188.69
WDZAN-YJY-3*6 | 16.6 | 216.42
WDZAN-YJY-3*10 | 19.5 | 298.65
WDZAN-YJY-3*16 | 21.6 | 366.44
WDZAN-YJY-3*25 | 25.8 | 522.79
WDZAN-YJY-3*35 | 27.8 | 606.99
WDZAN-YJY-3*50 | 32.7 | 839.82
WDZAN-YJY-3*70 | 37.6 | 1110.36
WDZAN-YJY-3*95 | 41.5 | 1352.65
WDZAN-YJY-3*120 | 45.2 | 1604.6
WDZAN-YJY-3*150 | 49.7 | 1940
WDZAN-YJY-3*185 | 54.6 | 2341.4
WDZAN-YJY-3*240 | 61.2 | 2941.66
WDZAN-YJY-3*300 | 67.2 | 3546.73
WDZAN-YJY-3*400 | 73.9 | 4289.22
WDZAN-YJY-4*1.5 | 14.6 | 167.42
WDZAN-YJY-4*2.5 | 15.5 | 188.69
WDZAN-YJY-4*4 | 16.6 | 216.42
WDZAN-YJY-4*6 | 17.8 | 248.85
WDZAN-YJY-4*10 | 21 | 346.36
WDZAN-YJY-4*16 | 23.5 | 433.74
WDZAN-YJY-4*25 | 28 | 615.75
WDZAN-YJY-4*35 | 30.3 | 721.07
WDZAN-YJY-4*50 | 35.8 | 1006.6
WDZAN-YJY-4*70 | 41.1 | 1326.7
WDZAN-YJY-4*95 | 45.6 | 1633.13
WDZAN-YJY-4*120 | 50.2 | 1979.23
WDZAN-YJY-4*150 | 54.6 | 2341.4
WDZAN-YJY-4*185 | 60.3 | 2855.78
WDZAN-YJY-4*240 | 67.6 | 3589.08
WDZAN-YJY-4*300 | 74.2 | 4324.12
WDZAN-YJY-4*400 | 82.1 | 5293.91
WDZAN-YJY-5*1.5 | 15.6 | 191.13
WDZAN-YJY-5*2.5 | 16.6 | 216.42
WDZAN-YJY-5*4 | 17.8 | 248.85
WDZAN-YJY-5*6 | 19.2 | 289.53
WDZAN-YJY-5*10 | 22.8 | 408.28
WDZAN-YJY-5*16 | 25.4 | 506.71
WDZAN-YJY-5*25 | 30.5 | 730.62
WDZAN-YJY-5*35 | 33 | 855.3
WDZAN-YJY-5*50 | 39.5 | 1225.42
WDZAN-YJY-5*70 | 44.9 | 1583.37
WDZAN-YJY-5*95 | 50.5 | 2002.96
WDZAN-YJY-5*120 | 55 | 2375.83
WDZAN-YJY-5*150 | 60 | 2827.43
WDZAN-YJY-5*185 | 66.8 | 3504.64
WDZAN-YJY-5*240 | 74.4 | 4347.46
WDZAN-YJY-5*300 | 82.1 | 5293.91
WDZAN-YJY-5*400 | 90.6 | 6446.83
WDZAN-YJY-3*2.5+1*1.5 | 15.3 | 183.85
WDZAN-YJY-3*4+1*2.5 | 16.3 | 208.67
WDZAN-YJY-3*6+1*4 | 17.5 | 240.53
WDZAN-YJY-3*10+1*6 | 20.3 | 323.65
WDZAN-YJY-3*16+1*10 | 22.8 | 408.28
WDZAN-YJY-3*25+1*16 | 27 | 572.56
WDZAN-YJY-3*35+1*16 | 28.7 | 646.92
WDZAN-YJY-3*50+1*25 | 34.2 | 918.63
WDZAN-YJY-3*70+1*35 | 38.9 | 1188.47
WDZAN-YJY-3*95+1*50 | 43.3 | 1472.54
WDZAN-YJY-3*120+1*70 | 47.6 | 1779.52
WDZAN-YJY-3*120+1*95 | 48.7 | 1862.72
WDZAN-YJY-3*150+1*70 | 51.3 | 2066.92
WDZAN-YJY-3*150+1*95 | 52.6 | 2173.01
WDZAN-YJY-3*185+1*95 | 56.7 | 2524.97
WDZAN-YJY-3*185+1*120 | 57.7 | 2614.82
WDZAN-YJY-3*240+1*120 | 63.4 | 3156.96
WDZAN-YJY-3*300+1*150 | 69.5 | 3793.67
WDZAN-YJY-3*400+1*185 | 76.4 | 4584.34
WDZAN-YJY-3*2.5+2*1.5 | 16.2 | 206.12
WDZAN-YJY-3*4+2*2.5 | 17.3 | 235.06
WDZAN-YJY-3*6+2*4 | 18.7 | 274.65
WDZAN-YJY-3*10+2*6 | 21.5 | 363.05
WDZAN-YJY-3*16+2*10 | 24.3 | 463.77
WDZAN-YJY-3*25+2*16 | 28.7 | 646.92
WDZAN-YJY-3*35+2*16 | 30.2 | 716.31
WDZAN-YJY-3*50+2*25 | 36.4 | 1040.62
WDZAN-YJY-3*70+2*35 | 41.2 | 1333.17
WDZAN-YJY-3*95+2*50 | 45.9 | 1654.68
WDZAN-YJY-3*120+2*70 | 51.2 | 2058.87
WDZAN-YJY-3*150+2*70 | 54.1 | 2298.71
WDZAN-YJY-3*150+2*95 | 56.2 | 2480.63
WDZAN-YJY-3*185+2*95 | 60 | 2827.43
WDZAN-YJY-3*240+2*120 | 66.9 | 3515.14
WDZAN-YJY-3*300+2*150 | 73.2 | 4208.35
WDZAN-YJY-3*400+2*185 | 81.2 | 5178.48
WDZAN-YJY-4*2.5+1*1.5 | 16.4 | 211.24
WDZAN-YJY-4*4+1*2.5 | 17.6 | 243.28
WDZAN-YJY-4*6+1*4 | 18.9 | 280.55
WDZAN-YJY-4*10+1*6 | 22.1 | 383.6
WDZAN-YJY-4*16+1*10 | 24.9 | 486.95
WDZAN-YJY-4*25+1*16 | 29.6 | 688.13
WDZAN-YJY-4*35+1*16 | 31.6 | 784.27
WDZAN-YJY-4*50+1*25 | 38 | 1134.11
WDZAN-YJY-4*70+1*35 | 43.2 | 1465.74
WDZAN-YJY-4*95+1*50 | 47.9 | 1802.03
WDZAN-YJY-4*120+1*70 | 53.2 | 2222.87
WDZAN-YJY-4*120+1*95 | 54.1 | 2298.71
WDZAN-YJY-4*150+1*70 | 57.1 | 2560.72
WDZAN-YJY-4*150+1*95 | 58 | 2642.08
WDZAN-YJY-4*185+1*95 | 63.6 | 3176.9
WDZAN-YJY-4*240+1*120 | 70.7 | 3925.8
WDZAN-YJY-4*300+1*150 | 77.5 | 4717.3
WDZAN-YJY-4*400+1*185 | 85.8 | 5781.82
WDZBN-YJY/WDZN-YJY/WDZCN-YJY/WDZDN-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘无卤低烟护套耐火电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
WDZN-YJY-1*1.5 | 6.3 | 31.17
WDZN-YJY-1*2.5 | 6.7 | 35.26
WDZN-YJY-1*4 | 7.1 | 39.59
WDZN-YJY-1*6 | 7.6 | 45.36
WDZN-YJY-1*10 | 8.8 | 60.82
WDZN-YJY-1*16 | 9.8 | 75.43
WDZN-YJY-1*25 | 11.5 | 103.87
WDZN-YJY-1*35 | 12.4 | 120.76
WDZN-YJY-1*50 | 13.8 | 149.57
WDZN-YJY-1*70 | 15.7 | 193.59
WDZN-YJY-1*95 | 17.7 | 246.06
WDZN-YJY-1*120 | 19.3 | 292.55
WDZN-YJY-1*150 | 21.2 | 352.99
WDZN-YJY-1*185 | 23.6 | 437.44
WDZN-YJY-1*240 | 26.5 | 551.55
WDZN-YJY-1*300 | 29 | 660.52
WDZN-YJY-1*400 | 32.3 | 819.4
WDZN-YJY-1*500 | 35.9 | 1012.23
WDZN-YJY-2*1.5 | 10.7 | 89.92
WDZN-YJY-2*2.5 | 11.4 | 102.07
WDZN-YJY-2*4 | 12.4 | 120.76
WDZN-YJY-2*6 | 13.4 | 141.03
WDZN-YJY-2*10 | 15.7 | 193.59
WDZN-YJY-2*16 | 17.7 | 246.06
WDZN-YJY-2*25 | 21.3 | 356.33
WDZN-YJY-2*35 | 23.1 | 419.1
WDZN-YJY-2*50 | 23.5 | 433.74
WDZN-YJY-2*70 | 26.3 | 543.25
WDZN-YJY-2*95 | 28.8 | 651.44
WDZN-YJY-2*120 | 31.5 | 779.31
WDZN-YJY-2*150 | 34.5 | 934.82
WDZN-YJY-2*185 | 37.9 | 1128.15
WDZN-YJY-2*240 | 41.8 | 1372.28
WDZN-YJY-2*300 | 45.3 | 1611.71
WDZN-YJY-2*400 | 50.9 | 2034.82
WDZN-YJY-3*1.5 | 11.2 | 98.52
WDZN-YJY-3*2.5 | 12 | 113.1
WDZN-YJY-3*4 | 13.1 | 134.78
WDZN-YJY-3*6 | 14.1 | 156.15
WDZN-YJY-3*10 | 16.7 | 219.04
WDZN-YJY-3*16 | 18.8 | 277.59
WDZN-YJY-3*25 | 22.6 | 401.15
WDZN-YJY-3*35 | 24.6 | 475.29
WDZN-YJY-3*50 | 30.4 | 725.83
WDZN-YJY-3*70 | 34.8 | 951.15
WDZN-YJY-3*95 | 38.7 | 1176.28
WDZN-YJY-3*120 | 42.4 | 1411.96
WDZN-YJY-3*150 | 46.5 | 1698.23
WDZN-YJY-3*185 | 51.4 | 2074.99
WDZN-YJY-3*240 | 57.6 | 2605.76
WDZN-YJY-3*300 | 63.6 | 3176.9
WDZN-YJY-3*400 | 70.4 | 3892.56
WDZN-YJY-4*1.5 | 12.1 | 114.99
WDZN-YJY-4*2.5 | 13.1 | 134.78
WDZN-YJY-4*4 | 14.2 | 158.37
WDZN-YJY-4*6 | 15.4 | 186.27
WDZN-YJY-4*10 | 18.2 | 260.16
WDZN-YJY-4*16 | 20.7 | 336.54
WDZN-YJY-4*25 | 24.9 | 486.95
WDZN-YJY-4*35 | 27.1 | 576.8
WDZN-YJY-4*50 | 33.4 | 876.16
WDZN-YJY-4*70 | 38.3 | 1152.09
WDZN-YJY-4*95 | 42.8 | 1438.72
WDZN-YJY-4*120 | 47 | 1734.94
WDZN-YJY-4*150 | 51.4 | 2074.99
WDZN-YJY-4*185 | 57.1 | 2560.72
WDZN-YJY-4*240 | 64 | 3216.99
WDZN-YJY-4*300 | 70.6 | 3914.71
WDZN-YJY-4*400 | 78.1 | 4790.62
WDZN-YJY-5*1.5 | 13.1 | 134.78
WDZN-YJY-5*2.5 | 14.1 | 156.15
WDZN-YJY-5*4 | 15.4 | 186.27
WDZN-YJY-5*6 | 16.8 | 221.67
WDZN-YJY-5*10 | 19.9 | 311.03
WDZN-YJY-5*16 | 22.6 | 401.15
WDZN-YJY-5*25 | 27.3 | 585.35
WDZN-YJY-5*35 | 29.8 | 697.46
WDZN-YJY-5*50 | 36.8 | 1063.62
WDZN-YJY-5*70 | 42.1 | 1392.05
WDZN-YJY-5*95 | 47.3 | 1757.16
WDZN-YJY-5*120 | 51.8 | 2107.41
WDZN-YJY-5*150 | 56.8 | 2533.88
WDZN-YJY-5*185 | 63.1 | 3127.15
WDZN-YJY-5*240 | 70.8 | 3936.92
WDZN-YJY-5*300 | 78.1 | 4790.62
WDZN-YJY-5*400 | 86.6 | 5890.14
WDZN-YJY-3*2.5+1*1.5 | 12.8 | 128.68
WDZN-YJY-3*4+1*2.5 | 13.9 | 151.75
WDZN-YJY-3*6+1*4 | 15.1 | 179.08
WDZN-YJY-3*10+1*6 | 17.6 | 243.28
WDZN-YJY-3*16+1*10 | 20.1 | 317.31
WDZN-YJY-3*25+1*16 | 23.9 | 448.63
WDZN-YJY-3*35+1*16 | 25.6 | 514.72
WDZN-YJY-3*50+1*25 | 31.8 | 794.23
WDZN-YJY-3*70+1*35 | 36.1 | 1023.54
WDZN-YJY-3*95+1*50 | 40.6 | 1294.62
WDZN-YJY-3*120+1*70 | 44.8 | 1576.33
WDZN-YJY-3*120+1*95 | 45.9 | 1654.68
WDZN-YJY-3*150+1*70 | 48.1 | 1817.11
WDZN-YJY-3*150+1*95 | 49.4 | 1916.65
WDZN-YJY-3*185+1*95 | 53.6 | 2256.42
WDZN-YJY-3*185+1*120 | 54.6 | 2341.4
WDZN-YJY-3*240+1*120 | 59.8 | 2808.62
WDZN-YJY-3*300+1*150 | 65.9 | 3410.83
WDZN-YJY-3*400+1*185 | 72.8 | 4162.48
WDZN-YJY-3*2.5+2*1.5 | 13.8 | 149.57
WDZN-YJY-3*4+2*2.5 | 14.9 | 174.37
WDZN-YJY-3*6+2*4 | 16.2 | 206.12
WDZN-YJY-3*10+2*6 | 18.7 | 274.65
WDZN-YJY-3*16+2*10 | 21.5 | 363.05
WDZN-YJY-3*25+2*16 | 25.5 | 510.71
WDZN-YJY-3*35+2*16 | 27 | 572.56
WDZN-YJY-3*50+2*25 | 34 | 907.92
WDZN-YJY-3*70+2*35 | 38.4 | 1158.12
WDZN-YJY-3*95+2*50 | 43.1 | 1458.96
WDZN-YJY-3*120+2*70 | 48 | 1809.56
WDZN-YJY-3*150+2*70 | 50.9 | 2034.82
WDZN-YJY-3*150+2*95 | 53 | 2206.18
WDZN-YJY-3*185+2*95 | 56.8 | 2533.88
WDZN-YJY-3*240+2*120 | 63.3 | 3147
WDZN-YJY-3*300+2*150 | 69.6 | 3804.59
WDZN-YJY-3*400+2*185 | 77.2 | 4680.85
WDZN-YJY-4*2.5+1*1.5 | 13.9 | 151.75
WDZN-YJY-4*4+1*2.5 | 15.2 | 181.46
WDZN-YJY-4*6+1*4 | 16.5 | 213.82
WDZN-YJY-4*10+1*6 | 19.3 | 292.55
WDZN-YJY-4*16+1*10 | 22.1 | 383.6
WDZN-YJY-4*25+1*16 | 26.4 | 547.39
WDZN-YJY-4*35+1*16 | 28.4 | 633.47
WDZN-YJY-4*50+1*25 | 35.2 | 973.14
WDZN-YJY-4*70+1*35 | 40.4 | 1281.9
WDZN-YJY-4*95+1*50 | 45.1 | 1597.51
WDZN-YJY-4*120+1*70 | 50 | 1963.5
WDZN-YJY-4*120+1*95 | 50.9 | 2034.82
WDZN-YJY-4*150+1*70 | 53.9 | 2281.75
WDZN-YJY-4*150+1*95 | 54.8 | 2358.58
WDZN-YJY-4*185+1*95 | 60 | 2827.43
WDZN-YJY-4*240+1*120 | 67 | 3525.65
WDZN-YJY-4*300+1*150 | 73.9 | 4289.22
WDZN-YJY-4*400+1*185 | 81.8 | 5255.29
ZA-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚乙烯护套电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
ZA-YJY-1*1.5 | 8 | 50.27
ZA-YJY-1*2.5 | 8.4 | 55.42
ZA-YJY-1*4 | 8.8 | 60.82
ZA-YJY-1*6 | 9.3 | 67.93
ZA-YJY-1*10 | 10.5 | 86.59
ZA-YJY-1*16 | 11.5 | 103.87
ZA-YJY-1*25 | 13.2 | 136.85
ZA-YJY-1*35 | 14.1 | 156.15
ZA-YJY-1*50 | 15.5 | 188.69
ZA-YJY-1*70 | 17.4 | 237.79
ZA-YJY-1*95 | 19.4 | 295.59
ZA-YJY-1*120 | 21 | 346.36
ZA-YJY-1*150 | 22.9 | 411.87
ZA-YJY-1*185 | 25.3 | 502.73
ZA-YJY-1*240 | 28.2 | 624.58
ZA-YJY-1*300 | 30.7 | 740.23
ZA-YJY-1*400 | 34.4 | 929.41
ZA-YJY-1*500 | 38 | 1134.11
ZA-YJY-2*1.5 | 11.8 | 109.36
ZA-YJY-2*2.5 | 12.6 | 124.69
ZA-YJY-2*4 | 13.5 | 143.14
ZA-YJY-2*6 | 14.5 | 165.13
ZA-YJY-2*10 | 17.2 | 232.35
ZA-YJY-2*16 | 19.2 | 289.53
ZA-YJY-2*25 | 23.1 | 419.1
ZA-YJY-2*35 | 25 | 490.87
ZA-YJY-2*50 | 26.6 | 555.72
ZA-YJY-2*70 | 27.3 | 585.35
ZA-YJY-2*95 | 30.3 | 721.07
ZA-YJY-2*120 | 33 | 855.3
ZA-YJY-2*150 | 36.1 | 1023.54
ZA-YJY-2*185 | 39.8 | 1244.1
ZA-YJY-2*240 | 43.7 | 1499.87
ZA-YJY-2*300 | 47.6 | 1779.52
ZA-YJY-2*400 | 53.2 | 2222.87
ZA-YJY-3*1.5 | 12.2 | 116.9
ZA-YJY-3*2.5 | 13.1 | 134.78
ZA-YJY-3*4 | 14.1 | 156.15
ZA-YJY-3*6 | 15.2 | 181.46
ZA-YJY-3*10 | 18.1 | 257.3
ZA-YJY-3*16 | 20.2 | 320.47
ZA-YJY-3*25 | 24.4 | 467.59
ZA-YJY-3*35 | 26.4 | 547.39
ZA-YJY-3*50 | 31.3 | 769.45
ZA-YJY-3*70 | 36.2 | 1029.22
ZA-YJY-3*95 | 40.1 | 1262.93
ZA-YJY-3*120 | 43.8 | 1506.74
ZA-YJY-3*150 | 48.3 | 1832.25
ZA-YJY-3*185 | 53.2 | 2222.87
ZA-YJY-3*240 | 59.8 | 2808.62
ZA-YJY-3*300 | 65.8 | 3400.49
ZA-YJY-3*400 | 72.5 | 4128.25
ZA-YJY-4*1.5 | 13 | 132.73
ZA-YJY-4*2.5 | 13.9 | 151.75
ZA-YJY-4*4 | 15 | 176.71
ZA-YJY-4*6 | 16.2 | 206.12
ZA-YJY-4*10 | 19.4 | 295.59
ZA-YJY-4*16 | 21.9 | 376.68
ZA-YJY-4*25 | 26.4 | 547.39
ZA-YJY-4*35 | 28.7 | 646.92
ZA-YJY-4*50 | 34.2 | 918.63
ZA-YJY-4*70 | 39.5 | 1225.42
ZA-YJY-4*95 | 44 | 1520.53
ZA-YJY-4*120 | 48.6 | 1855.08
ZA-YJY-4*150 | 53 | 2206.18
ZA-YJY-4*185 | 58.7 | 2706.24
ZA-YJY-4*240 | 66 | 3421.19
ZA-YJY-4*300 | 72.6 | 4139.65
ZA-YJY-4*400 | 80.5 | 5089.58
ZA-YJY-5*1.5 | 13.8 | 149.57
ZA-YJY-5*2.5 | 14.8 | 172.03
ZA-YJY-5*4 | 16 | 201.06
ZA-YJY-5*6 | 17.4 | 237.79
ZA-YJY-5*10 | 21 | 346.36
ZA-YJY-5*16 | 23.6 | 437.44
ZA-YJY-5*25 | 28.7 | 646.92
ZA-YJY-5*35 | 31.2 | 764.54
ZA-YJY-5*50 | 37.7 | 1116.28
ZA-YJY-5*70 | 43.1 | 1458.96
ZA-YJY-5*95 | 48.7 | 1862.72
ZA-YJY-5*120 | 53.2 | 2222.87
ZA-YJY-5*150 | 58.2 | 2660.33
ZA-YJY-5*185 | 65 | 3318.31
ZA-YJY-5*240 | 72.6 | 4139.65
ZA-YJY-5*300 | 80.3 | 5064.32
ZA-YJY-5*400 | 88.8 | 6193.21
ZA-YJY-3*2.5+1*1.5 | 13.7 | 147.41
ZA-YJY-3*4+1*2.5 | 14.7 | 169.72
ZA-YJY-3*6+1*4 | 15.9 | 198.56
ZA-YJY-3*10+1*6 | 18.7 | 274.65
ZA-YJY-3*16+1*10 | 21.2 | 352.99
ZA-YJY-3*25+1*16 | 25.4 | 506.71
ZA-YJY-3*35+1*16 | 27.1 | 576.8
ZA-YJY-3*50+1*25 | 32.6 | 834.69
ZA-YJY-3*70+1*35 | 37.3 | 1092.72
ZA-YJY-3*95+1*50 | 41.7 | 1365.72
ZA-YJY-3*120+1*70 | 46 | 1661.9
ZA-YJY-3*120+1*95 | 47.1 | 1742.34
ZA-YJY-3*150+1*70 | 49.7 | 1940
ZA-YJY-3*150+1*95 | 51 | 2042.82
ZA-YJY-3*185+1*95 | 55.1 | 2384.48
ZA-YJY-3*185+1*120 | 56.1 | 2471.81
ZA-YJY-3*240+1*120 | 61.8 | 2999.62
ZA-YJY-3*300+1*150 | 67.9 | 3621.01
ZA-YJY-3*400+1*185 | 74.8 | 4394.33
ZA-YJY-3*2.5+2*1.5 | 14.4 | 162.86
ZA-YJY-3*4+2*2.5 | 15.5 | 188.69
ZA-YJY-3*6+2*4 | 16.9 | 224.32
ZA-YJY-3*10+2*6 | 19.7 | 304.81
ZA-YJY-3*16+2*10 | 22.5 | 397.61
ZA-YJY-3*25+2*16 | 26.9 | 568.32
ZA-YJY-3*35+2*16 | 28.4 | 633.47
ZA-YJY-3*50+2*25 | 34.6 | 940.25
ZA-YJY-3*70+2*35 | 39.4 | 1219.22
ZA-YJY-3*95+2*50 | 44.1 | 1527.45
ZA-YJY-3*120+2*70 | 49.4 | 1916.65
ZA-YJY-3*150+2*70 | 52.3 | 2148.29
ZA-YJY-3*150+2*95 | 54.4 | 2324.28
ZA-YJY-3*185+2*95 | 58.2 | 2660.33
ZA-YJY-3*240+2*120 | 65.1 | 3328.53
ZA-YJY-3*300+2*150 | 71.4 | 4003.93
ZA-YJY-3*400+2*185 | 79.4 | 4951.43
ZA-YJY-4*2.5+1*1.5 | 14.6 | 167.42
ZA-YJY-4*4+1*2.5 | 15.8 | 196.07
ZA-YJY-4*6+1*4 | 17.1 | 229.66
ZA-YJY-4*10+1*6 | 20.3 | 323.65
ZA-YJY-4*16+1*10 | 23.1 | 419.1
ZA-YJY-4*25+1*16 | 27.8 | 606.99
ZA-YJY-4*35+1*16 | 29.8 | 697.46
ZA-YJY-4*50+1*25 | 36.2 | 1029.22
ZA-YJY-4*70+1*35 | 41.4 | 1346.14
ZA-YJY-4*95+1*50 | 46.1 | 1669.14
ZA-YJY-4*120+1*70 | 51.4 | 2074.99
ZA-YJY-4*120+1*95 | 52.3 | 2148.29
ZA-YJY-4*150+1*70 | 55.3 | 2401.82
ZA-YJY-4*150+1*95 | 56.2 | 2480.63
ZA-YJY-4*185+1*95 | 61.8 | 2999.62
ZA-YJY-4*240+1*120 | 68.9 | 3728.45
ZA-YJY-4*300+1*150 | 75.7 | 4500.72
ZA-YJY-4*400+1*185 | 84 | 5541.77
ZB-YJY/ZC-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚乙烯护套电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
ZA-YJV-1*1.5 | 5.6 | 24.63
ZA-YJV-1*2.5 | 6 | 28.27
ZA-YJV-1*4 | 6.4 | 32.17
ZA-YJV-1*6 | 6.9 | 37.39
ZA-YJV-1*10 | 8.1 | 51.53
ZA-YJV-1*16 | 9.1 | 65.04
ZA-YJV-1*25 | 10.8 | 91.61
ZA-YJV-1*35 | 11.7 | 107.51
ZA-YJV-1*50 | 13.1 | 134.78
ZA-YJV-1*70 | 15 | 176.71
ZA-YJV-1*95 | 17 | 226.98
ZA-YJV-1*120 | 18.6 | 271.72
ZA-YJV-1*150 | 20.5 | 330.06
ZA-YJV-1*185 | 22.9 | 411.87
ZA-YJV-1*240 | 25.8 | 522.79
ZA-YJV-1*300 | 28.3 | 629.02
ZA-YJV-1*400 | 31.6 | 784.27
ZA-YJV-1*500 | 35.2 | 973.14
ZA-YJV-2*1.5 | 9.4 | 69.4
ZA-YJV-2*2.5 | 10.1 | 80.12
ZA-YJV-2*4 | 11.1 | 96.77
ZA-YJV-2*6 | 12.1 | 114.99
ZA-YJV-2*10 | 14.4 | 162.86
ZA-YJV-2*16 | 16.4 | 211.24
ZA-YJV-2*25 | 20 | 314.16
ZA-YJV-2*35 | 21.8 | 373.25
ZA-YJV-2*50 | 22.2 | 387.08
ZA-YJV-2*70 | 25 | 490.87
ZA-YJV-2*95 | 27.5 | 593.96
ZA-YJV-2*120 | 30.2 | 716.31
ZA-YJV-2*150 | 33.2 | 865.7
ZA-YJV-2*185 | 36.6 | 1052.09
ZA-YJV-2*240 | 40.5 | 1288.25
ZA-YJV-2*300 | 44 | 1520.53
ZA-YJV-2*400 | 49.6 | 1932.21
ZA-YJV-3*1.5 | 9.8 | 75.43
ZA-YJV-3*2.5 | 10.6 | 88.25
ZA-YJV-3*4 | 11.7 | 107.51
ZA-YJV-3*6 | 12.7 | 126.68
ZA-YJV-3*10 | 15.3 | 183.85
ZA-YJV-3*16 | 17.4 | 237.79
ZA-YJV-3*25 | 21.2 | 352.99
ZA-YJV-3*35 | 23.2 | 422.73
ZA-YJV-3*50 | 29 | 660.52
ZA-YJV-3*70 | 33.4 | 876.16
ZA-YJV-3*95 | 37.3 | 1092.72
ZA-YJV-3*120 | 41 | 1320.25
ZA-YJV-3*150 | 45.1 | 1597.51
ZA-YJV-3*185 | 50 | 1963.5
ZA-YJV-3*240 | 56.2 | 2480.63
ZA-YJV-3*300 | 62.2 | 3038.58
ZA-YJV-3*400 | 69 | 3739.28
ZA-YJV-4*1.5 | 10.5 | 86.59
ZA-YJV-4*2.5 | 11.5 | 103.87
ZA-YJV-4*4 | 12.6 | 124.69
ZA-YJV-4*6 | 13.8 | 149.57
ZA-YJV-4*10 | 16.6 | 216.42
ZA-YJV-4*16 | 19.1 | 286.52
ZA-YJV-4*25 | 23.3 | 426.38
ZA-YJV-4*35 | 25.5 | 510.71
ZA-YJV-4*50 | 31.8 | 794.23
ZA-YJV-4*70 | 36.7 | 1057.84
ZA-YJV-4*95 | 41.2 | 1333.17
ZA-YJV-4*120 | 45.4 | 1618.83
ZA-YJV-4*150 | 49.8 | 1947.82
ZA-YJV-4*185 | 55.5 | 2419.22
ZA-YJV-4*240 | 62.4 | 3058.15
ZA-YJV-4*300 | 69 | 3739.28
ZA-YJV-4*400 | 76.5 | 4596.35
ZA-YJV-5*1.5 | 11.3 | 100.29
ZA-YJV-5*2.5 | 12.3 | 118.82
ZA-YJV-5*4 | 13.6 | 145.27
ZA-YJV-5*6 | 15 | 176.71
ZA-YJV-5*10 | 18.1 | 257.3
ZA-YJV-5*16 | 20.8 | 339.79
ZA-YJV-5*25 | 25.5 | 510.71
ZA-YJV-5*35 | 28 | 615.75
ZA-YJV-5*50 | 35 | 962.11
ZA-YJV-5*70 | 40.3 | 1275.56
ZA-YJV-5*95 | 45.5 | 1625.97
ZA-YJV-5*120 | 50 | 1963.5
ZA-YJV-5*150 | 55 | 2375.83
ZA-YJV-5*185 | 61.3 | 2951.28
ZA-YJV-5*240 | 69 | 3739.28
ZA-YJV-5*300 | 76.3 | 4572.34
ZA-YJV-5*400 | 84.8 | 5647.83
ZA-YJV-3*2.5+1*1.5 | 11.2 | 98.52
ZA-YJV-3*4+1*2.5 | 12.3 | 118.82
ZA-YJV-3*6+1*4 | 13.5 | 143.14
ZA-YJV-3*10+1*6 | 16 | 201.06
ZA-YJV-3*16+1*10 | 18.5 | 268.8
ZA-YJV-3*25+1*16 | 22.3 | 390.57
ZA-YJV-3*35+1*16 | 24 | 452.39
ZA-YJV-3*50+1*25 | 30.2 | 716.31
ZA-YJV-3*70+1*35 | 34.5 | 934.82
ZA-YJV-3*95+1*50 | 39 | 1194.59
ZA-YJV-3*120+1*70 | 43.2 | 1465.74
ZA-YJV-3*120+1*95 | 44.3 | 1541.34
ZA-YJV-3*150+1*70 | 46.5 | 1698.23
ZA-YJV-3*150+1*95 | 47.8 | 1794.51
ZA-YJV-3*185+1*95 | 52 | 2123.72
ZA-YJV-3*185+1*120 | 53 | 2206.18
ZA-YJV-3*240+1*120 | 58.2 | 2660.33
ZA-YJV-3*300+1*150 | 64.3 | 3247.22
ZA-YJV-3*400+1*185 | 71.2 | 3981.53
ZA-YJV-3*2.5+2*1.5 | 12 | 113.1
ZA-YJV-3*4+2*2.5 | 13.1 | 134.78
ZA-YJV-3*6+2*4 | 14.4 | 162.86
ZA-YJV-3*10+2*6 | 16.9 | 224.32
ZA-YJV-3*16+2*10 | 19.7 | 304.81
ZA-YJV-3*25+2*16 | 23.7 | 441.15
ZA-YJV-3*35+2*16 | 25.2 | 498.76
ZA-YJV-3*50+2*25 | 32.2 | 814.33
ZA-YJV-3*70+2*35 | 36.6 | 1052.09
ZA-YJV-3*95+2*50 | 41.3 | 1339.65
ZA-YJV-3*120+2*70 | 46.2 | 1676.39
ZA-YJV-3*150+2*70 | 49.1 | 1893.45
ZA-YJV-3*150+2*95 | 51.2 | 2058.87
ZA-YJV-3*185+2*95 | 55 | 2375.83
ZA-YJV-3*240+2*120 | 61.5 | 2970.57
ZA-YJV-3*300+2*150 | 67.8 | 3610.35
ZA-YJV-3*400+2*185 | 75.4 | 4465.11
ZA-YJV-4*2.5+1*1.5 | 12.1 | 114.99
ZA-YJV-4*4+1*2.5 | 13.4 | 141.03
ZA-YJV-4*6+1*4 | 14.7 | 169.72
ZA-YJV-4*10+1*6 | 17.5 | 240.53
ZA-YJV-4*16+1*10 | 20.3 | 323.65
ZA-YJV-4*25+1*16 | 24.6 | 475.29
ZA-YJV-4*35+1*16 | 26.6 | 555.72
ZA-YJV-4*50+1*25 | 33.4 | 876.16
ZA-YJV-4*70+1*35 | 38.6 | 1170.21
ZA-YJV-4*95+1*50 | 43.3 | 1472.54
ZA-YJV-4*120+1*70 | 48.2 | 1824.67
ZA-YJV-4*120+1*95 | 49.1 | 1893.45
ZA-YJV-4*150+1*70 | 52.1 | 2131.89
ZA-YJV-4*150+1*95 | 53 | 2206.18
ZA-YJV-4*185+1*95 | 58.2 | 2660.33
ZA-YJV-4*240+1*120 | 65.2 | 3338.76
ZA-YJV-4*300+1*150 | 72.1 | 4082.82
ZA-YJV-4*400+1*185 | 80 | 5026.55
ZAN-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚乙烯护套耐火电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
ZAN-YJY-1*1.5 | 6.3 | 31.17
ZAN-YJY-1*2.5 | 6.7 | 35.26
ZAN-YJY-1*4 | 7.1 | 39.59
ZAN-YJY-1*6 | 7.6 | 45.36
ZAN-YJY-1*10 | 8.8 | 60.82
ZAN-YJY-1*16 | 9.8 | 75.43
ZAN-YJY-1*25 | 11.5 | 103.87
ZAN-YJY-1*35 | 12.4 | 120.76
ZAN-YJY-1*50 | 13.8 | 149.57
ZAN-YJY-1*70 | 15.7 | 193.59
ZAN-YJY-1*95 | 17.7 | 246.06
ZAN-YJY-1*120 | 19.3 | 292.55
ZAN-YJY-1*150 | 21.2 | 352.99
ZAN-YJY-1*185 | 23.6 | 437.44
ZAN-YJY-1*240 | 26.5 | 551.55
ZAN-YJY-1*300 | 29 | 660.52
ZAN-YJY-1*400 | 32.3 | 819.4
ZAN-YJY-1*500 | 35.9 | 1012.23
ZAN-YJY-2*1.5 | 10.7 | 89.92
ZAN-YJY-2*2.5 | 11.4 | 102.07
ZAN-YJY-2*4 | 12.4 | 120.76
ZAN-YJY-2*6 | 13.4 | 141.03
ZAN-YJY-2*10 | 15.7 | 193.59
ZAN-YJY-2*16 | 17.7 | 246.06
ZAN-YJY-2*25 | 21.3 | 356.33
ZAN-YJY-2*35 | 23.1 | 419.1
ZAN-YJY-2*50 | 23.5 | 433.74
ZAN-YJY-2*70 | 26.3 | 543.25
ZAN-YJY-2*95 | 28.8 | 651.44
ZAN-YJY-2*120 | 31.5 | 779.31
ZAN-YJY-2*150 | 34.5 | 934.82
ZAN-YJY-2*185 | 37.9 | 1128.15
ZAN-YJY-2*240 | 41.8 | 1372.28
ZAN-YJY-2*300 | 45.3 | 1611.71
ZAN-YJY-2*400 | 50.9 | 2034.82
ZAN-YJY-3*1.5 | 11.2 | 98.52
ZAN-YJY-3*2.5 | 12 | 113.1
ZAN-YJY-3*4 | 13.1 | 134.78
ZAN-YJY-3*6 | 14.1 | 156.15
ZAN-YJY-3*10 | 16.7 | 219.04
ZAN-YJY-3*16 | 18.8 | 277.59
ZAN-YJY-3*25 | 22.6 | 401.15
ZAN-YJY-3*35 | 24.6 | 475.29
ZAN-YJY-3*50 | 30.4 | 725.83
ZAN-YJY-3*70 | 34.8 | 951.15
ZAN-YJY-3*95 | 38.7 | 1176.28
ZAN-YJY-3*120 | 42.4 | 1411.96
ZAN-YJY-3*150 | 46.5 | 1698.23
ZAN-YJY-3*185 | 51.4 | 2074.99
ZAN-YJY-3*240 | 57.6 | 2605.76
ZAN-YJY-3*300 | 63.6 | 3176.9
ZAN-YJY-3*400 | 70.4 | 3892.56
ZAN-YJY-4*1.5 | 12.1 | 114.99
ZAN-YJY-4*2.5 | 13.1 | 134.78
ZAN-YJY-4*4 | 14.2 | 158.37
ZAN-YJY-4*6 | 15.4 | 186.27
ZAN-YJY-4*10 | 18.2 | 260.16
ZAN-YJY-4*16 | 20.7 | 336.54
ZAN-YJY-4*25 | 24.9 | 486.95
ZAN-YJY-4*35 | 27.1 | 576.8
ZAN-YJY-4*50 | 33.4 | 876.16
ZAN-YJY-4*70 | 38.3 | 1152.09
ZAN-YJY-4*95 | 42.8 | 1438.72
ZAN-YJY-4*120 | 47 | 1734.94
ZAN-YJY-4*150 | 51.4 | 2074.99
ZAN-YJY-4*185 | 57.1 | 2560.72
ZAN-YJY-4*240 | 64 | 3216.99
ZAN-YJY-4*300 | 70.6 | 3914.71
ZAN-YJY-4*400 | 78.1 | 4790.62
ZAN-YJY-5*1.5 | 13.1 | 134.78
ZAN-YJY-5*2.5 | 14.1 | 156.15
ZAN-YJY-5*4 | 15.4 | 186.27
ZAN-YJY-5*6 | 16.8 | 221.67
ZAN-YJY-5*10 | 19.9 | 311.03
ZAN-YJY-5*16 | 22.6 | 401.15
ZAN-YJY-5*25 | 27.3 | 585.35
ZAN-YJY-5*35 | 29.8 | 697.46
ZAN-YJY-5*50 | 36.8 | 1063.62
ZAN-YJY-5*70 | 42.1 | 1392.05
ZAN-YJY-5*95 | 47.3 | 1757.16
ZAN-YJY-5*120 | 51.8 | 2107.41
ZAN-YJY-5*150 | 56.8 | 2533.88
ZAN-YJY-5*185 | 63.1 | 3127.15
ZAN-YJY-5*240 | 70.8 | 3936.92
ZAN-YJY-5*300 | 78.1 | 4790.62
ZAN-YJY-5*400 | 86.6 | 5890.14
ZAN-YJY-3*2.5+1*1.5 | 12.8 | 128.68
ZAN-YJY-3*4+1*2.5 | 13.9 | 151.75
ZAN-YJY-3*6+1*4 | 15.1 | 179.08
ZAN-YJY-3*10+1*6 | 17.6 | 243.28
ZAN-YJY-3*16+1*10 | 20.1 | 317.31
ZAN-YJY-3*25+1*16 | 23.9 | 448.63
ZAN-YJY-3*35+1*16 | 25.6 | 514.72
ZAN-YJY-3*50+1*25 | 31.8 | 794.23
ZAN-YJY-3*70+1*35 | 36.1 | 1023.54
ZAN-YJY-3*95+1*50 | 40.6 | 1294.62
ZAN-YJY-3*120+1*70 | 44.8 | 1576.33
ZAN-YJY-3*120+1*95 | 45.9 | 1654.68
ZAN-YJY-3*150+1*70 | 48.1 | 1817.11
ZAN-YJY-3*150+1*95 | 49.4 | 1916.65
ZAN-YJY-3*185+1*95 | 53.6 | 2256.42
ZAN-YJY-3*185+1*120 | 54.6 | 2341.4
ZAN-YJY-3*240+1*120 | 59.8 | 2808.62
ZAN-YJY-3*300+1*150 | 65.9 | 3410.83
ZAN-YJY-3*400+1*185 | 72.8 | 4162.48
ZAN-YJY-3*2.5+2*1.5 | 13.8 | 149.57
ZAN-YJY-3*4+2*2.5 | 14.9 | 174.37
ZAN-YJY-3*6+2*4 | 16.2 | 206.12
ZAN-YJY-3*10+2*6 | 18.7 | 274.65
ZAN-YJY-3*16+2*10 | 21.5 | 363.05
ZAN-YJY-3*25+2*16 | 25.5 | 510.71
ZAN-YJY-3*35+2*16 | 27 | 572.56
ZAN-YJY-3*50+2*25 | 34 | 907.92
ZAN-YJY-3*70+2*35 | 38.4 | 1158.12
ZAN-YJY-3*95+2*50 | 43.1 | 1458.96
ZAN-YJY-3*120+2*70 | 48 | 1809.56
ZAN-YJY-3*150+2*70 | 50.9 | 2034.82
ZAN-YJY-3*150+2*95 | 53 | 2206.18
ZAN-YJY-3*185+2*95 | 56.8 | 2533.88
ZAN-YJY-3*240+2*120 | 63.3 | 3147
ZAN-YJY-3*300+2*150 | 69.6 | 3804.59
ZAN-YJY-3*400+2*185 | 77.2 | 4680.85
ZAN-YJY-4*2.5+1*1.5 | 13.9 | 151.75
ZAN-YJY-4*4+1*2.5 | 15.2 | 181.46
ZAN-YJY-4*6+1*4 | 16.5 | 213.82
ZAN-YJY-4*10+1*6 | 19.3 | 292.55
ZAN-YJY-4*16+1*10 | 22.1 | 383.6
ZAN-YJY-4*25+1*16 | 26.4 | 547.39
ZAN-YJY-4*35+1*16 | 28.4 | 633.47
ZAN-YJY-4*50+1*25 | 35.2 | 973.14
ZAN-YJY-4*70+1*35 | 40.4 | 1281.9
ZAN-YJY-4*95+1*50 | 45.1 | 1597.51
ZAN-YJY-4*120+1*70 | 50 | 1963.5
ZAN-YJY-4*120+1*95 | 50.9 | 2034.82
ZAN-YJY-4*150+1*70 | 53.9 | 2281.75
ZAN-YJY-4*150+1*95 | 54.8 | 2358.58
ZAN-YJY-4*185+1*95 | 60 | 2827.43
ZAN-YJY-4*240+1*120 | 67 | 3525.65
ZAN-YJY-4*300+1*150 | 73.9 | 4289.22
ZAN-YJY-4*400+1*185 | 81.8 | 5255.29
ZBN-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚乙烯护套耐火电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
ZBN-YJY-1*1.5 | 10.1 | 80.12
ZBN-YJY-1*2.5 | 10.5 | 86.59
ZBN-YJY-1*4 | 10.9 | 93.31
ZBN-YJY-1*6 | 11.4 | 102.07
ZBN-YJY-1*10 | 12.6 | 124.69
ZBN-YJY-1*16 | 13.6 | 145.27
ZBN-YJY-1*25 | 15.3 | 183.85
ZBN-YJY-1*35 | 16.2 | 206.12
ZBN-YJY-1*50 | 17.5 | 240.53
ZBN-YJY-1*70 | 19.7 | 304.81
ZBN-YJY-1*95 | 21.7 | 369.84
ZBN-YJY-1*120 | 23.3 | 426.38
ZBN-YJY-1*150 | 25.2 | 498.76
ZBN-YJY-1*185 | 27.3 | 585.35
ZBN-YJY-1*240 | 30.3 | 721.07
ZBN-YJY-1*300 | 33 | 855.3
ZBN-YJY-1*400 | 36.1 | 1023.54
ZBN-YJY-1*500 | 42.7 | 1432.01
ZBN-YJY-2*1.5 | 14.3 | 160.61
ZBN-YJY-2*2.5 | 15 | 176.71
ZBN-YJY-2*4 | 16 | 201.06
ZBN-YJY-2*6 | 17 | 226.98
ZBN-YJY-2*10 | 19.3 | 292.55
ZBN-YJY-2*16 | 21.3 | 356.33
ZBN-YJY-2*25 | 24.6 | 475.29
ZBN-YJY-2*35 | 26.5 | 551.55
ZBN-YJY-2*50 | 26.1 | 535.02
ZBN-YJY-2*70 | 29 | 660.52
ZBN-YJY-2*95 | 31.4 | 774.37
ZBN-YJY-2*120 | 37 | 1075.21
ZBN-YJY-2*150 | 40.1 | 1262.93
ZBN-YJY-2*185 | 43.4 | 1479.34
ZBN-YJY-2*240 | 47.3 | 1757.16
ZBN-YJY-2*300 | 50.8 | 2026.83
ZBN-YJY-2*400 | 56.4 | 2498.32
ZBN-YJY-3*1.5 | 14.8 | 172.03
ZBN-YJY-3*2.5 | 15.6 | 191.13
ZBN-YJY-3*4 | 16.6 | 216.42
ZBN-YJY-3*6 | 17.7 | 246.06
ZBN-YJY-3*10 | 20.3 | 323.65
ZBN-YJY-3*16 | 22.4 | 394.08
ZBN-YJY-3*25 | 26 | 530.93
ZBN-YJY-3*35 | 28 | 615.75
ZBN-YJY-3*50 | 32.9 | 850.12
ZBN-YJY-3*70 | 37.6 | 1110.36
ZBN-YJY-3*95 | 44.4 | 1548.3
ZBN-YJY-3*120 | 48.1 | 1817.11
ZBN-YJY-3*150 | 52 | 2123.72
ZBN-YJY-3*185 | 57.1 | 2560.72
ZBN-YJY-3*240 | 63.1 | 3127.15
ZBN-YJY-3*300 | 69.1 | 3750.13
ZBN-YJY-3*400 | 75.8 | 4512.62
ZBN-YJY-4*1.5 | 15.7 | 193.59
ZBN-YJY-4*2.5 | 16.7 | 219.04
ZBN-YJY-4*4 | 17.8 | 248.85
ZBN-YJY-4*6 | 19 | 283.53
ZBN-YJY-4*10 | 21.8 | 373.25
ZBN-YJY-4*16 | 24.3 | 463.77
ZBN-YJY-4*25 | 28.2 | 624.58
ZBN-YJY-4*35 | 30.6 | 735.42
ZBN-YJY-4*50 | 36 | 1017.88
ZBN-YJY-4*70 | 43.8 | 1506.74
ZBN-YJY-4*95 | 48.6 | 1855.08
ZBN-YJY-4*120 | 52.6 | 2173.01
ZBN-YJY-4*150 | 57.1 | 2560.72
ZBN-YJY-4*185 | 62.6 | 3077.79
ZBN-YJY-4*240 | 69.6 | 3804.59
ZBN-YJY-4*300 | 76.1 | 4548.41
ZBN-YJY-4*400 | 83.6 | 5489.12
ZBN-YJY-5*1.5 | 16.8 | 221.67
ZBN-YJY-5*2.5 | 17.8 | 248.85
ZBN-YJY-5*4 | 19 | 283.53
ZBN-YJY-5*6 | 20.4 | 326.85
ZBN-YJY-5*10 | 23.5 | 433.74
ZBN-YJY-5*16 | 26.2 | 539.13
ZBN-YJY-5*25 | 30.8 | 745.06
ZBN-YJY-5*35 | 33.4 | 876.16
ZBN-YJY-5*50 | 39.3 | 1213.04
ZBN-YJY-5*70 | 47.6 | 1779.52
ZBN-YJY-5*95 | 52.8 | 2189.56
ZBN-YJY-5*120 | 57.8 | 2623.89
ZBN-YJY-5*150 | 62.3 | 3048.36
ZBN-YJY-5*185 | 68.8 | 3717.64
ZBN-YJY-5*240 | 76.3 | 4572.34
ZBN-YJY-5*300 | 83.8 | 5515.41
ZBN-YJY-5*400 | 92.1 | 6662.07
ZBN-YJY-3*2.5+1*1.5 | 16.4 | 211.24
ZBN-YJY-3*4+1*2.5 | 17.5 | 240.53
ZBN-YJY-3*6+1*4 | 18.7 | 274.65
ZBN-YJY-3*10+1*6 | 21.1 | 349.67
ZBN-YJY-3*16+1*10 | 23.6 | 437.44
ZBN-YJY-3*25+1*16 | 27.2 | 581.07
ZBN-YJY-3*35+1*16 | 28.9 | 655.97
ZBN-YJY-3*50+1*25 | 34.6 | 940.25
ZBN-YJY-3*70+1*35 | 38.9 | 1188.47
ZBN-YJY-3*95+1*50 | 46 | 1661.9
ZBN-YJY-3*120+1*70 | 50.3 | 1987.13
ZBN-YJY-3*120+1*95 | 51.6 | 2091.17
ZBN-YJY-3*150+1*70 | 53.8 | 2273.29
ZBN-YJY-3*150+1*95 | 54.9 | 2367.2
ZBN-YJY-3*185+1*95 | 59 | 2733.97
ZBN-YJY-3*185+1*120 | 60.2 | 2846.31
ZBN-YJY-3*240+1*120 | 65.3 | 3349.01
ZBN-YJY-3*300+1*150 | 71.6 | 4026.39
ZBN-YJY-3*400+1*185 | 78.6 | 4852.16
ZBN-YJY-3*2.5+2*1.5 | 17.3 | 235.06
ZBN-YJY-3*4+2*2.5 | 18.5 | 268.8
ZBN-YJY-3*6+2*4 | 19.8 | 307.91
ZBN-YJY-3*10+2*6 | 22.3 | 390.57
ZBN-YJY-3*16+2*10 | 25.1 | 494.81
ZBN-YJY-3*25+2*16 | 28.9 | 655.97
ZBN-YJY-3*35+2*16 | 30.4 | 725.83
ZBN-YJY-3*50+2*25 | 36.6 | 1052.09
ZBN-YJY-3*70+2*35 | 41.2 | 1333.17
ZBN-YJY-3*95+2*50 | 48.6 | 1855.08
ZBN-YJY-3*120+2*70 | 53.5 | 2248.01
ZBN-YJY-3*150+2*70 | 56.4 | 2498.32
ZBN-YJY-3*150+2*95 | 58.5 | 2687.83
ZBN-YJY-3*185+2*95 | 62.3 | 3048.36
ZBN-YJY-3*240+2*120 | 68.8 | 3717.64
ZBN-YJY-3*300+2*150 | 75.1 | 4429.65
ZBN-YJY-3*400+2*185 | 82.8 | 5384.56
ZBN-YJY-4*2.5+1*1.5 | 17.5 | 240.53
ZBN-YJY-4*4+1*2.5 | 18.8 | 277.59
ZBN-YJY-4*6+1*4 | 20.1 | 317.31
ZBN-YJY-4*10+1*6 | 22.9 | 411.87
ZBN-YJY-4*16+1*10 | 25.8 | 522.79
ZBN-YJY-4*25+1*16 | 29.8 | 697.46
ZBN-YJY-4*35+1*16 | 31.8 | 794.23
ZBN-YJY-4*50+1*25 | 38 | 1134.11
ZBN-YJY-4*70+1*35 | 45.9 | 1654.68
ZBN-YJY-4*95+1*50 | 50.6 | 2010.9
ZBN-YJY-4*120+1*70 | 55.5 | 2419.22
ZBN-YJY-4*120+1*95 | 56.4 | 2498.32
ZBN-YJY-4*150+1*70 | 59.4 | 2771.17
ZBN-YJY-4*150+1*95 | 60.5 | 2874.75
ZBN-YJY-4*185+1*95 | 65.5 | 3369.55
ZBN-YJY-4*240+1*120 | 72.5 | 4128.25
ZBN-YJY-4*300+1*150 | 79.4 | 4951.43
ZBN-YJY-4*400+1*185 | 87.3 | 5985.75
ZCN-YJY 额定电压 0.6/1KV及以下铜芯交联聚乙烯绝缘聚乙烯护套耐火电力电缆
电缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
ZCN-YJY-1*1.5 | 10.7 | 89.92
ZCN-YJY-1*2.5 | 11.1 | 96.77
ZCN-YJY-1*4 | 11.5 | 103.87
ZCN-YJY-1*6 | 12 | 113.1
ZCN-YJY-1*10 | 13.3 | 138.93
ZCN-YJY-1*16 | 14.3 | 160.61
ZCN-YJY-1*25 | 15.9 | 198.56
ZCN-YJY-1*35 | 16.8 | 221.67
ZCN-YJY-1*50 | 19.7 | 304.81
ZCN-YJY-1*70 | 21.6 | 366.44
ZCN-YJY-1*95 | 23.5 | 433.74
ZCN-YJY-1*120 | 26 | 530.93
ZCN-YJY-1*150 | 27.7 | 602.63
ZCN-YJY-1*185 | 30.1 | 711.58
ZCN-YJY-1*240 | 32.9 | 850.12
ZCN-YJY-1*300 | 35.5 | 989.8
ZCN-YJY-1*400 | 39.9 | 1250.36
ZCN-YJY-1*500 | 43.5 | 1486.17
ZCN-YJY-2*1.5 | 15.5 | 188.69
ZCN-YJY-2*2.5 | 16.3 | 208.67
ZCN-YJY-2*4 | 17.2 | 232.35
ZCN-YJY-2*6 | 18.3 | 263.02
ZCN-YJY-2*10 | 21.6 | 366.44
ZCN-YJY-2*16 | 23.6 | 437.44
ZCN-YJY-2*25 | 27.8 | 606.99
ZCN-YJY-2*35 | 29.7 | 692.79
ZCN-YJY-2*50 | 33.6 | 886.68
ZCN-YJY-2*70 | 37.8 | 1122.21
ZCN-YJY-2*95 | 42.7 | 1432.01
ZCN-YJY-2*120 | 46.1 | 1669.14
ZCN-YJY-2*150 | 49.6 | 1932.21
ZCN-YJY-2*185 | 55.8 | 2445.45
ZCN-YJY-2*240 | 61.5 | 2970.57
ZCN-YJY-2*300 | 67.2 | 3546.73
ZCN-YJY-2*400 | 73.4 | 4231.38
ZCN-YJY-3*1.5 | 16.2 | 206.12
ZCN-YJY-3*2.5 | 17 | 226.98
ZCN-YJY-3*4 | 18 | 254.47
ZCN-YJY-3*6 | 19.1 | 286.52
ZCN-YJY-3*10 | 22.7 | 404.71
ZCN-YJY-3*16 | 24.8 | 483.05
ZCN-YJY-3*25 | 29.3 | 674.26
ZCN-YJY-3*35 | 31.3 | 769.45
ZCN-YJY-3*50 | 35.6 | 995.38
ZCN-YJY-3*70 | 41.2 | 1333.17
ZCN-YJY-3*95 | 45.3 | 1611.71
ZCN-YJY-3*120 | 48.9 | 1878.05
ZCN-YJY-3*150 | 54.3 | 2315.74
ZCN-YJY-3*185 | 59.3 | 2761.84
ZCN-YJY-3*240 | 65.8 | 3400.49
ZCN-YJY-3*300 | 71.7 | 4037.65
ZCN-YJY-3*400 | 78.2 | 4802.9
ZCN-YJY-4*1.5 | 17.2 | 232.35
ZCN-YJY-4*2.5 | 18.2 | 260.16
ZCN-YJY-4*4 | 19.3 | 292.55
ZCN-YJY-4*6 | 21.5 | 363.05
ZCN-YJY-4*10 | 24.4 | 467.59
ZCN-YJY-4*16 | 27.5 | 593.96
ZCN-YJY-4*25 | 31.7 | 789.24
ZCN-YJY-4*35 | 34.1 | 913.27
ZCN-YJY-4*50 | 38.8 | 1182.37
ZCN-YJY-4*70 | 45.1 | 1597.51
ZCN-YJY-4*95 | 49.5 | 1924.42
ZCN-YJY-4*120 | 55.1 | 2384.48
ZCN-YJY-4*150 | 59.4 | 2771.17
ZCN-YJY-4*185 | 65 | 3318.31
ZCN-YJY-4*240 | 72.3 | 4105.5
ZCN-YJY-4*300 | 78.8 | 4876.88
ZCN-YJY-4*400 | 87.9 | 6068.31
ZCN-YJY-5*1.5 | 18.4 | 265.9
ZCN-YJY-5*2.5 | 19.4 | 295.59
ZCN-YJY-5*4 | 21.6 | 366.44
ZCN-YJY-5*6 | 22.8 | 408.28
ZCN-YJY-5*10 | 26.3 | 543.25
ZCN-YJY-5*16 | 29.7 | 692.79
ZCN-YJY-5*25 | 34.3 | 924.01
ZCN-YJY-5*35 | 37 | 1075.21
ZCN-YJY-5*50 | 43.4 | 1479.34
ZCN-YJY-5*70 | 49 | 1885.74
ZCN-YJY-5*95 | 55.3 | 2401.82
ZCN-YJY-5*120 | 60 | 2827.43
ZCN-YJY-5*150 | 64.9 | 3308.1
ZCN-YJY-5*185 | 71.6 | 4026.39
ZCN-YJY-5*240 | 79.2 | 4926.52
ZCN-YJY-5*300 | 88.2 | 6109.8
ZCN-YJY-5*400 | 96.5 | 7313.82
ZCN-YJY-3*2.5+1*1.5 | 17.9 | 251.65
ZCN-YJY-3*4+1*2.5 | 19 | 283.53
ZCN-YJY-3*6+1*4 | 21.1 | 349.67
ZCN-YJY-3*10+1*6 | 23.7 | 441.15
ZCN-YJY-3*16+1*10 | 26.2 | 539.13
ZCN-YJY-3*25+1*16 | 30.7 | 740.23
ZCN-YJY-3*35+1*16 | 32.4 | 824.48
ZCN-YJY-3*50+1*25 | 37.2 | 1086.87
ZCN-YJY-3*70+1*35 | 42.9 | 1445.45
ZCN-YJY-3*95+1*50 | 47.1 | 1742.34
ZCN-YJY-3*120+1*70 | 51.5 | 2083.07
ZCN-YJY-3*120+1*95 | 53.5 | 2248.01
ZCN-YJY-3*150+1*70 | 56.1 | 2471.81
ZCN-YJY-3*150+1*95 | 57.2 | 2569.7
ZCN-YJY-3*185+1*95 | 61.5 | 2970.57
ZCN-YJY-3*185+1*120 | 62.5 | 3067.96
ZCN-YJY-3*240+1*120 | 68.1 | 3642.37
ZCN-YJY-3*300+1*150 | 74 | 4300.84
ZCN-YJY-3*400+1*185 | 82.3 | 5319.73
ZCN-YJY-3*2.5+2*1.5 | 19 | 283.53
ZCN-YJY-3*4+2*2.5 | 21.1 | 349.67
ZCN-YJY-3*6+2*4 | 22.4 | 394.08
ZCN-YJY-3*10+2*6 | 25 | 490.87
ZCN-YJY-3*16+2*10 | 28.6 | 642.42
ZCN-YJY-3*25+2*16 | 32.6 | 834.69
ZCN-YJY-3*35+2*16 | 34.1 | 913.27
ZCN-YJY-3*50+2*25 | 39.6 | 1231.63
ZCN-YJY-3*70+2*35 | 45.1 | 1597.51
ZCN-YJY-3*95+2*50 | 49.8 | 1947.82
ZCN-YJY-3*120+2*70 | 56.2 | 2480.63
ZCN-YJY-3*150+2*70 | 59.1 | 2743.25
ZCN-YJY-3*150+2*95 | 61.2 | 2941.66
ZCN-YJY-3*185+2*95 | 64.9 | 3308.1
ZCN-YJY-3*240+2*120 | 71.8 | 4048.92
ZCN-YJY-3*300+2*150 | 78.1 | 4790.62
ZCN-YJY-3*400+2*185 | 87.3 | 5985.75
ZCN-YJY-4*2.5+1*1.5 | 19.2 | 289.53
ZCN-YJY-4*4+1*2.5 | 21.3 | 356.33
ZCN-YJY-4*6+1*4 | 22.7 | 404.71
ZCN-YJY-4*10+1*6 | 25.6 | 514.72
ZCN-YJY-4*16+1*10 | 29.1 | 665.08
ZCN-YJY-4*25+1*16 | 33.4 | 876.16
ZCN-YJY-4*35+1*16 | 35.6 | 995.38
ZCN-YJY-4*50+1*25 | 42.2 | 1398.67
ZCN-YJY-4*70+1*35 | 47.1 | 1742.34
ZCN-YJY-4*95+1*50 | 51.9 | 2115.56
ZCN-YJY-4*120+1*70 | 58 | 2642.08
ZCN-YJY-4*120+1*95 | 59.1 | 2743.25
ZCN-YJY-4*150+1*70 | 62 | 3019.07
ZCN-YJY-4*150+1*95 | 63 | 3117.25
ZCN-YJY-4*185+1*95 | 68.5 | 3685.28
ZCN-YJY-4*240+1*120 | 75.5 | 4476.97
ZCN-YJY-4*300+1*150 | 79.4 | 4951.43
ZCN-YJY-4*400+1*185 | 87.3 | 5985.75

## 长飞
光缆
光缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
2芯室内光缆 | 4 | 12.57 | 室内光缆
4芯室内光缆 | 4.8 | 18.1
6芯室内光缆 | 5.1 | 20.43
8芯室内光缆 | 5.6 | 24.63
12芯室内光缆 | 6.2 | 30.19
24芯室内光缆 | 8.1 | 51.53
36芯室内光缆 | 14.5 | 165.13
48芯室内光缆 | 14.8 | 172.03
72芯室内光缆 | 17.5 | 240.53
96芯室内光缆 | 20.7 | 336.54
144芯室内光缆 | 24.8 | 483.05
2~30芯室外光缆 | 7.8 | 47.78 | 室外光缆-松套层绞式非铠装光缆
32~36芯室外光缆 | 8.1 | 51.53
38~60芯室外光缆 | 9.2 | 66.48
62~72芯室外光缆 | 9.6 | 72.38
74~96芯室外光缆 | 11 | 95.03
98~120芯室外光缆 | 12 | 113.1
122~144芯室外光缆 | 13.2 | 136.85
146~216芯室外光缆 | 13.7 | 147.41
288芯室外光缆 | 15.5 | 188.69

## 天诚
铜缆
线缆名称 | 线缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
安防专用非屏蔽双绞线 | UTP-CAT.5E Plus | 5 | 19.63
非屏蔽双绞线 | UTP-CAT.5E | 5.3 | 22.06
屏蔽双绞线 | FTP-CAT.5E | 6.5 | 33.18
双屏蔽双绞线 | SFTP-CAT.5E | 7 | 38.48
交联护套屏蔽多股双绞线 | SFTP-CAT.5E | 7 | 38.48
非屏蔽双绞线 23AWG | UTP-CAT.6 | 6 | 28.27
非屏蔽双绞线 24AWG | UTP-CAT.6 | 6 | 28.27
防啮齿非屏蔽双绞线 | UTP-CAT.6 | 6 | 28.27
非屏蔽双绞线 | UTP-CAT.6 Plus | 6.2 | 30.19
屏蔽双绞线 | FTP-CAT.6 | 7.6 | 45.36
防啮齿屏蔽双绞线 | FTP-CAT.6 | 7.5 | 44.18
室内外野战屏蔽双绞线 | FTP-CAT.6 | 7.5 | 44.18
对对屏蔽双绞线 | U/FTP-CAT.6 | 8 | 50.27
双屏蔽双绞线 | SFTP-CAT.6 | 8 | 50.27
交联护套屏蔽多股双绞线 | SFTP-CAT.6 | 9 | 63.62
非连续铝箔非屏蔽双绞线 | UTP-CAT.6A | 7.4 | 43.01
非屏蔽双绞线 | UTP-CAT.6A | 8.4 | 55.42
屏蔽双绞线 | FTP-CAT.6A | 7.3 | 41.85
室内外野战屏蔽双绞线 | FTP-CAT.6A | 8 | 50.27
对对屏蔽双绞线 | U/FTP-CAT.6A | 7.5 | 44.18
双屏蔽双绞线 | SFTP-CAT.6A | 8.2 | 52.81
屏蔽双绞线 | S/FTP-CAT.7 | 7.5 | 44.18
屏蔽双绞线 | S/FTP-CAT.7A | 7.8 | 47.78
屏蔽双绞线 | S/FTP-CAT.8 | 8.2 | 52.81
蝶形光缆（皮线光缆）
线缆名称 | 线缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
金属加强低烟无卤 | GJXH-02B6 | 2.0*3.0 | 6
非金属加强低烟无卤 | GJXFH-02B6 | 2.0*3.0 | 6
金属加强低烟无卤阻燃 | GJXZH-02B6 | 2.0*3.0 | 6
非金属加强低烟无卤阻燃 | GJXFZH-02B6 | 2.0*3.0 | 6
YXB音箱线
线缆名称 | 线缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
| YXB-0.24 | 2.6*5.1 | 13.26
| YXB-0.4 | 3.1*6.1 | 18.91
| YXB-0.5 | 3.3*6.5 | 21.45
| YXB-0.55 | 3.6*7.1 | 25.56
| YXB-0.7 | 3.6*7.1 | 25.56
| YXB-0.8 | 4.1*8.1 | 33.21
| YXB-1.0 | 4.1*8.1 | 33.21
| YXB-1.2 | 4.1*8.1 | 33.21
| YXB-1.5 | 4.1*8.1 | 33.21
| YXB-1.54 | 4.1*8.1 | 33.21
| YXB-2.5 | 5.1*10.1 | 51.51
| YXB-5.0 | 6.0*12.1 | 72.6
GYX工程音响线
线缆名称 | 线缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
| GYX-2*1.0 | 8.4 | 55.42
| GYX-2*1.5 | 8.72 | 59.72
| GYX-2*2.0 | 9.14 | 65.61
| GYX-2*2.5 | 9.62 | 72.68
| GYX-2*3.0 | 10.9 | 93.31
| GYX-2*3.5 | 11.32 | 100.64
| GYX-2*4.0 | 12.08 | 114.61
| GYX-4*1.0 | 9.68 | 73.59
| GYX-4*1.5 | 10.47 | 86.1
| GYX-4*2.0 | 10.98 | 94.69
| GYX-4*2.5 | 11.56 | 104.96
| GYX-4*3.0 | 12.62 | 125.09
| GYX-4*3.5 | 13.33 | 139.56
| GYX-4*4.0 | 14.24 | 159.26
HTP话筒线
线缆名称 | 线缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
铝箔+铜丝编织 | HTP-2*20/0.10 | 6 | 28.27
铝箔+铜丝编织 | HTP-2*27/0.10 | 6 | 28.27
铝箔+铜丝编织 | HTP-2*37/0.10 | 6 | 28.27
铝箔+铜丝编织 | HTP-2*48/0.10 | 6 | 28.27
铝箔+铜丝编织 | HTP-3*20/0.10 | 6.15 | 29.71
铝箔+铜丝编织 | HTP-3*27/0.10 | 6.05 | 28.75
铝箔+铜丝编织 有铜丝缠绕和面纱缠绕 | HTP-2*37/0.10 | 6 | 28.27
HBYV、HBYY型电话线
线缆名称 | 线缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
1对 | HBYV-1*2*0.4 | 1.75*2.55 | 4.4625
1对 | HBYV-1*2*0.5 | 1.87*2.77 | 5.1799
2对 | HBYV-2*2*0.4 | 3.05*4.2 | 12.81
2对 | HBYV-2*2*0.5 | 3.05*4.7 | 14.335
电梯线缆
线缆名称 | 线缆型号 | 最大外径 （mm） | 电缆截面积 （mm2）
超五类非屏蔽网线+RVV2*0.75 | TUTP-G1 | 8.5*22.0 | 187
2芯皮线光缆+2*RY1.0 | TGDFH2B6+2*1.0-G1 | 4.5*19.5 | 87.75

## RD
规格 | 外径 | 截面积 | 根数
2芯皮线光缆 | 3 | 6 | 0
2芯室内光缆 | 4 | 12.5664 | 0
4芯室内光缆 | 4.8 | 18.0956 | 1
6芯室内光缆 | 5.1 | 20.4282 | 0
8芯室内光缆 | 5.6 | 24.6301 | 0
12芯室内光缆 | 6.2 | 30.1907 | 0
24芯室内光缆 | 8.1 | 51.53 | 0
36芯室内光缆 | 14.5 | 165.13 | 0
48芯室内光缆 | 14.8 | 172.0336 | 0
72芯室内光缆 | 17.5 | 240.5282 | 0
96芯室内光缆 | 20.7 | 336.5353 | 0
144芯室内光缆 | 24.8 | 483.0513 | 0
2~30芯室外光缆 | 7.8 | 47.7836 | 0
32~36芯室外光缆 | 8.1 | 51.53 | 0
38~60芯室外光缆 | 9.2 | 66.4761 | 0
62~72芯室外光缆 | 9.6 | 72.3823 | 0
74~96芯室外光缆 | 11 | 95.0332 | 0
98~120芯室外光缆 | 12 | 113.0973 | 0
122~144芯室外光缆 | 13.2 | 136.8478 | 0
146~216芯室外光缆 | 13.7 | 147.4114 | 0
288芯室外光缆 | 15.5 | 188.6919 | 0
3类25对大对数 | 11.6 | 105.6832 | 0
3类50对大对数 | 16.5 | 213.8246 | 0
3类100对大对数 | 21.2 | 352.9894 | 0
5类25对大对数 | 12.5 | 122.7185 | 0
UTP-CAT.5E | 5.3 | 22.0618 | 0
FTP-CAT.5E | 6.5 | 33.1831 | 0
SFTP-CAT.5E | 7 | 38.4845 | 0
UTP-CAT.6 | 6 | 28.2743 | 0
FTP-CAT.6 | 7.6 | 45.3646 | 0
U/FTP-CAT.6 | 8 | 50.2655 | 0
SFTP-CAT.6 | 8 | 50.2655 | 0
UTP-CAT.6A | 8.4 | 55.4177 | 0
FTP-CAT.6A | 7.3 | 41.8539 | 0
U/FTP-CAT.6A | 7.5 | 44.1786 | 0
SFTP-CAT.6A | 8.2 | 52.8102 | 0
S/FTP-CAT.7 | 7.5 | 44.1786 | 0
S/FTP-CAT.7A | 7.8 | 47.7836 | 0
S/FTP-CAT.8 | 8.2 | 52.8102 | 0
HBYV-1*2*0.4 | 2.55 | 4.4625 | 0
HBYV-1*2*0.5 | 2.77 | 5.1799 | 0
HBYV-2*2*0.4 | 4.2 | 12.81 | 0
HBYV-2*2*0.5 | 4.7 | 14.335 | 0
RVV-2*0.5 | 5.9 | 27.3397 | 0
RVV-2*0.75 | 6.3 | 31.1725 | 0
RVV-2*1.0 | 7.5 | 44.1786 | 0
RVV-2*1.5 | 8.6 | 58.088 | 0
RVV-2*2.5 | 10.6 | 88.2473 | 0
RVV-4*0.75 | 8.3 | 54.1061 | 0
RVV-4*1.0 | 9 | 63.6173 | 0
RVV-4*1.5 | 10.5 | 86.5901 | 0
RVV-4*2.5 | 12.5 | 122.7185 | 0
RVV-6*0.75 | 9.6 | 72.3823 | 0
RVV-6*1.0 | 11 | 95.0332 | 0
RVV-6*1.5 | 13.3 | 138.9291 | 0
RVV-6*2.5 | 15.8 | 196.0668 | 0
RVV-8*0.75 | 10.6 | 88.2473 | 0
RVV-8*1.0 | 13.2 | 136.8478 | 0
RVV-8*1.5 | 14.2 | 158.3677 | 0
RVV-8*2.5 | 17.7 | 246.0574 | 0
RVS-2*0.5 | 6 | 28.2743 | 0
RVS-2*0.75 | 6.2 | 30.1907 | 0
RVS-2*1.0 | 6.6 | 34.2119 | 0
RVS-2*1.5 | 7.2 | 40.715 | 0
RVS-2*2.5 | 8.2 | 52.8102 | 0
RVVP-2*0.5 | 6.8 | 36.3168 | 0
RVVP-2*0.75 | 7.4 | 43.0084 | 0
RVVP-2*1.0 | 8.2 | 52.8102 | 0
RVVP-2*1.5 | 9.2 | 66.4761 | 0
RVVP-2*2.5 | 11.7 | 107.5132 | 0
RVVP-4*0.5 | 8.9 | 62.2114 | 0
RVVP-4*0.75 | 9.3 | 67.9291 | 0
RVVP-4*1.0 | 10.5 | 86.5901 | 0
RVVP-4*1.5 | 11.5 | 103.8689 | 0
RVVP-4*2.5 | 13.6 | 145.2672 | 0
RVVP-6*0.5 | 10.2 | 81.7128 | 0
RVVP-6*0.75 | 10.7 | 89.9202 | 0
RVVP-6*1.0 | 12.4 | 120.7628 | 0
RVVP-6*1.5 | 13.6 | 145.2672 | 0
RVVP-6*2.5 | 16.1 | 203.5831 | 0
RVVP-8*0.5 | 11.2 | 98.5203 | 0
RVVP-8*0.75 | 11.8 | 109.3588 | 0
RVVP-8*1.0 | 13.7 | 147.4114 | 0
RVVP-8*1.5 | 15 | 176.7146 | 0
RVVP-8*2.5 | 18 | 254.469 | 0
RVSP-2*0.5 | 6.9 | 37.3928 | 0
RVSP-2*0.75 | 7.4 | 43.0084 | 0
RVSP-2*1.0 | 8.2 | 52.8102 | 0
RVSP-2*1.5 | 9.4 | 69.3978 | 0
RVSP-2*2.5 | 11.5 | 103.8689 | 0
HTP-2*20/0.10 | 6 | 28.2743 | 0
HTP-2*27/0.10 | 6 | 28.2743 | 0
HTP-2*37/0.10 | 6 | 28.2743 | 0
HTP-2*48/0.10 | 6 | 28.2743 | 0
HTP-3*20/0.10 | 6.15 | 29.7057 | 0
HTP-3*27/0.10 | 6.05 | 28.7475 | 0
GYX-2*1.0 | 8.4 | 55.4177 | 0
GYX-2*1.5 | 8.72 | 59.7204 | 0
GYX-2*2.0 | 9.14 | 65.6118 | 0
GYX-2*2.5 | 9.62 | 72.6842 | 0
GYX-2*3.0 | 10.9 | 93.3132 | 0
GYX-2*3.5 | 11.32 | 100.6428 | 0
GYX-2*4.0 | 12.08 | 114.6103 | 0
SYV-75-5 | 7.5 | 44.1786 | 0
SYV-75-7 | 11.6 | 105.6832 | 0
SYV-75-9 | 12.6 | 124.6898 | 0
SYV-75-12 | 15.4 | 186.265 | 0
SYWV-75-5 | 7.5 | 44.1786 | 0
SYWV-75-7 | 10.6 | 88.2473 | 0
SYWV-75-9 | 12.6 | 124.6898 | 0
TUTP-G1 | 22 | 187 | 0
TGDFH2B6+2*1.0-G1 | 19.5 | 87.75 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1/2"馈线 HCAAYZ 50-12射频同轴电缆 | 15.7 | 193.5928 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0

## QD
规格 | 外径 | 截面积 | 根数
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!